## Request a quote
Request a quotation for 0.6/1 kV Multi-Core AL EBXL-XLPE/HFFR
Share governing standard (IEC/VDE/UL WTTC/GB/T), voltage rating (0.6/1 kV, 1.8/3 kV or 2,000 V), conductor (Cu or Al) × cross-section, torsion angle and drum length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/0-6-1kv-multi-core-al-ebxl-xlpe-hffr-tower-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
0.6/1 kV Multi-Core (3C / 3.5C / 4C) Stranded Aluminum EBXL-XLPE / HFF – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1kv-multi-core-al-ebxl-xlpe-hffr-tower-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Max. pulling kN ≈ | Min. bend R mm | Series
| 0.6/1 kV Multi-Core AL 1×150 / 4×95 Al | 1 × 150 mm² (or 4 × 95 mm² Al) | Class 2 Compacted Al / Class 5 AA8000 | 23.5 | 640 | 10.5 | 190 | 0.6/1 kV Multi-Core AL EBXL-XLPE/HFFR Construction Schedule (−40…+105 °C)
| 0.6/1 kV Multi-Core AL 1×240 / 4×150 Al | 1 × 240 mm² (or 4 × 150 mm² Al) | Class 2 Compacted Al / Class 5 AA8000 | 28.4 | 980 | 16.8 | 230 | 0.6/1 kV Multi-Core AL EBXL-XLPE/HFFR Construction Schedule (−40…+105 °C)
| 0.6/1 kV Multi-Core AL 1×400 / 4×240 Al | 1 × 400 mm² (or 4 × 240 mm² Al) | Class 2 Compacted Al / Class 5 AA8000 | 35.8 | 1590 | 28 | 290 | 0.6/1 kV Multi-Core AL EBXL-XLPE/HFFR Construction Schedule (−40…+105 °C)
Custom conductor cross-sections, core counts, pre-lugged tower kits and drum lengths available per IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification.

## Electrical & thermal parameters
0.6/1 kV Multi-Core (3C / 3.5C / 4C) Stranded Aluminum EBXL-XLPE / HFF – Electrical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1kv-multi-core-al-ebxl-xlpe-hffr-tower-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ Ω/km | Rating / Impedance | Operating temp.
1 × 150 mm² (or 4 × 95 mm² Al) | 0.206 | 0.6/1 kV (315 A Al) | −40…+105 °C
1 × 240 mm² (or 4 × 150 mm² Al) | 0.125 | 0.6/1 kV (435 A Al) | −40…+105 °C
1 × 400 mm² (or 4 × 240 mm² Al) | 0.0778 | 0.6/1 kV (590 A Al) | −40…+105 °C
Every production length undergoes routine conductor DC resistance, AC high-voltage spark/dielectric and dimensional verification.

## Technical data
0.6/1 kV Multi-Core (3C / 3.5C / 4C) Stranded Aluminum EBXL-XLPE / HFF – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1kv-multi-core-al-ebxl-xlpe-hffr-tower-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Tested per IEC 60502-1 / IEC 60332-3)
Key data | Operating temp. | −40…+105 °C (Cold-climate & nacelle wind service)
Key data | Min. bend radius | 10 × OD (Drip-loop, hub & tower routing)
Key data | Core / conductor | Stranded Aluminu (Lightweight aluminum phase & neutral con)
Key data | Outer protection | HFFR / HF-PO Zer (Flame-retardant low-smoke polyolefin jac)
Key data | Standard | IEC 60502-1 / IE (IEC 60502-1 & IEC 60332-3 Multi-Core Alu)
Electrical | Rated voltage / operating system | 0.6/1 kV (IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification)
Electrical | Core / conductor construction | Stranded Aluminum Conductors (3C / 3.5C / 4C) — Lightweight aluminum phase & neutral conductors (16-400 mm²)
Electrical | Primary dielectric / insulation | EBXL-XLPE Cross-Linked Polyethylene Insulation — High-thermal-stability electron-beam cross-linked XLPE
Thermal | Continuous operating temperature | −40…+105 °C (wind turbine nacelle, hub & tower duty)
Thermal | Low-temperature torsion & cold bend | Verified cold-flex and torsion endurance across −40…+105 °C per IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel cable drum
Mechanical | Outer jacket / sheath protection | HFFR / HF-PO Zero-Halogen Outer Sheath — Flame-retardant low-smoke polyolefin jacket for tower distribution
Mechanical | Minimum bending radius | 10 × OD
Mechanical | Intermediate screen / separator / core layer | EBXL-XLPE Cross-Linked Polyethylene Insulation — High-thermal-stability electron-beam cross-linked XLPE
Resistance | Oil, grease, ozone & UV resistance | Resistant to wind turbine gearbox oil, hydraulic fluid, ozone and UV weathering per IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification
Resistance | Flame retardancy & smoke/halogen emission | Flame-retardant and environmental performance verified per IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification
Standards | Conductor & flame/test standards | IEC 60228 / IEC 60332-1-2 & -3 / UL 2277 WTTC / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | 0.6/1 kV Multi-Core AL EBXL-XLPE/HFFR
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (HFFR / HF-PO Zer)
Identification | Customs tariff (HS) | 8544.49 / 8544.60

## Construction
0.6/1 kV Multi-Core (3C / 3.5C / 4C) Stranded Aluminum EBXL-XLPE / HFF – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1kv-multi-core-al-ebxl-xlpe-hffr-tower-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded Aluminum Conductors (3C / 3.5C | Lightweight aluminum phase & neutral conductors (16-400 mm²)
2 | EBXL-XLPE Cross-Linked Polyethylene Insu | High-thermal-stability electron-beam cross-linked XLPE
3 | HFFR / HF-PO Zero-Halogen Outer Sheath | Flame-retardant low-smoke polyolefin jacket for tower distribution
| 0.6/1 kV Multi-Core AL EBXL-XLPE/HFFR — Standard Wind Turbine Execution | Built to IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification with stranded aluminum conductors (3c / 3.5c / 4c) and hffr / hf-po zero-halogen outer sheath
| 0.6/1 kV Multi-Core AL EBXL-XLPE/HFFR — Pre-Cut Tower / Drip-Loop Kit | Available on bulk export reels or pre-cut to turbine tower section and nacelle drip-loop lengths
| 0.6/1 kV Multi-Core AL EBXL-XLPE/HFFR — Cold Torsion & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, conductor DC resistance & cold-torsion qualification report

## Quality and supply
0.6/1 kV Multi-Core (3C / 3.5C / 4C) Stranded Aluminum EBXL-XLPE / HFF – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1kv-multi-core-al-ebxl-xlpe-hffr-tower-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification) — DC resistance at 20 °C and insulation/sheath wall thickness within IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification limits | Every manufactured drum length
Routine test | AC high-voltage dielectric & insulation resistance test (IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification) — Zero dielectric breakdown and verified insulation resistance for 0.6/1 kV rating | Every manufactured drum length
Type test | Low-temperature drip-loop torsion, oil & flame qualification (IEC 60502-1 & IEC 60332-3 Multi-Core Aluminum EBXL-XLPE/HFFR Wind Tower Specification) — Verified cold torsion cycle endurance, oil resistance and flame retardancy across −40…+105 °C | Type qualification & periodic lot audit
Standard / approval | IEC 60502-1 / IEC 60332-3 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 0.6/1 kV Multi-Core AL EBXL-XLPE/HFFR IEC 60502-1 / IEC 60332-3 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel reels or pre-cut wind turbine tower & drip-loop kits
Supply | Standard lengths: 500 m, 1,000 m or custom cut-to-length nacelle drip-loop and tower section sets
Supply | MOQ: 100 m (standard configurations) · 300 m (custom wind builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP