## Request a quote
Request a quotation for 1.8/3 (3.6) kV EPR/PCP Torsion
Share governing standard (IEC/VDE/UL WTTC/GB/T), voltage rating (0.6/1 kV, 1.8/3 kV or 2,000 V), conductor (Cu or Al) × cross-section, torsion angle and drum length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/1-8-3-3-6-kv-flexible-rubber-torsion-wind-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
1.8/3 (3.6) kV 3GI3 EPR / LSOH & Polychloroprene Flexible Rubber Wind – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3-3-6-kv-flexible-rubber-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Max. pulling kN ≈ | Min. bend R mm | Series
| 1.8/3 (3.6) kV EPR/PCP 1×95 / 4G25 Cu | 1 × 95 mm² (or 4G25 mm² / 3/0 AWG) | IEC 60228 Class 5 Flexible Cu/SnCu | 21.6 | 1080 | 14.2 | 110 | 1.8/3 (3.6) kV EPR/PCP Torsion Construction Schedule (−40…+90 °C)
| 1.8/3 (3.6) kV EPR/PCP 1×185 / 4G50 Cu | 1 × 185 mm² (or 4G50 mm² / 373 kcmil) | IEC 60228 Class 5 Flexible Cu/SnCu | 27.8 | 1960 | 27.5 | 140 | 1.8/3 (3.6) kV EPR/PCP Torsion Construction Schedule (−40…+90 °C)
| 1.8/3 (3.6) kV EPR/PCP 1×300 / 4G95 Cu | 1 × 300 mm² (or 1×535/777 kcmil) | IEC 60228 Class 5 Flexible Cu/SnCu | 34.6 | 3120 | 45 | 175 | 1.8/3 (3.6) kV EPR/PCP Torsion Construction Schedule (−40…+90 °C)
Custom conductor cross-sections, core counts, pre-lugged tower kits and drum lengths available per IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification.

## Electrical & thermal parameters
1.8/3 (3.6) kV 3GI3 EPR / LSOH & Polychloroprene Flexible Rubber Wind – Electrical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3-3-6-kv-flexible-rubber-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ Ω/km | Rating / Impedance | Operating temp.
1 × 95 mm² (or 4G25 mm² / 3/0 AWG) | 0.206 | 1.8/3 (3.6) kV (320 A Cu) | −40…+90 °C
1 × 185 mm² (or 4G50 mm² / 373 kcmil) | 0.106 | 1.8/3 (3.6) kV (495 A Cu) | −40…+90 °C
1 × 300 mm² (or 1×535/777 kcmil) | 0.0641 | 1.8/3 (3.6) kV (680 A Cu) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, AC high-voltage spark/dielectric and dimensional verification.

## Technical data
1.8/3 (3.6) kV 3GI3 EPR / LSOH & Polychloroprene Flexible Rubber Wind – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3-3-6-kv-flexible-rubber-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.8/3 (3.6) kV (Tested per IEC 60502-1 / VDE 0250)
Key data | Operating temp. | −40…+90 °C (Cold-climate & nacelle wind service)
Key data | Min. bend radius | 5 × OD (Drip-loop, hub & tower routing)
Key data | Core / conductor | IEC 60228 Class (Plain or tinned flexible copper cores (2)
Key data | Outer protection | LSOH / Polychlor (Cold-resistant (-40 °C to +90 °C) dynami)
Key data | Standard | IEC 60502-1 / VD (IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic )
Electrical | Rated voltage / operating system | 1.8/3 (3.6) kV (IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification)
Electrical | Core / conductor construction | IEC 60228 Class 5 Flexible Copper Conductors — Plain or tinned flexible copper cores (25-400 mm²)
Electrical | Primary dielectric / insulation | 1.8/3 (3.6) kV 3GI3 EPR Core Insulation — Cross-linked ethylene-propylene rubber primary insulation
Thermal | Continuous operating temperature | −40…+90 °C (wind turbine nacelle, hub & tower duty)
Thermal | Low-temperature torsion & cold bend | Verified cold-flex and torsion endurance across −40…+90 °C per IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel cable drum
Mechanical | Outer jacket / sheath protection | LSOH / Polychloroprene (PCP) Torsion Jacket — Cold-resistant (-40 °C to +90 °C) dynamic torsion outer sheath
Mechanical | Minimum bending radius | 5 × OD
Mechanical | Intermediate screen / separator / core layer | 1.8/3 (3.6) kV 3GI3 EPR Core Insulation — Cross-linked ethylene-propylene rubber primary insulation
Resistance | Oil, grease, ozone & UV resistance | Resistant to wind turbine gearbox oil, hydraulic fluid, ozone and UV weathering per IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification
Resistance | Flame retardancy & smoke/halogen emission | Flame-retardant and environmental performance verified per IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification
Standards | Conductor & flame/test standards | IEC 60228 / IEC 60332-1-2 & -3 / UL 2277 WTTC / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | 1.8/3 (3.6) kV EPR/PCP Torsion
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (LSOH / Polychlor)
Identification | Customs tariff (HS) | 8544.49 / 8544.60

## Construction
1.8/3 (3.6) kV 3GI3 EPR / LSOH & Polychloroprene Flexible Rubber Wind – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3-3-6-kv-flexible-rubber-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | IEC 60228 Class 5 Flexible Copper Conduc | Plain or tinned flexible copper cores (25-400 mm²)
2 | 1.8/3 (3.6) kV 3GI3 EPR Core Insulation | Cross-linked ethylene-propylene rubber primary insulation
3 | LSOH / Polychloroprene (PCP) Torsion Jac | Cold-resistant (-40 °C to +90 °C) dynamic torsion outer sheath
| 1.8/3 (3.6) kV EPR/PCP Torsion — Standard Wind Turbine Execution | Built to IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification with iec 60228 class 5 flexible copper conductors and lsoh / polychloroprene (pcp) torsion jacket
| 1.8/3 (3.6) kV EPR/PCP Torsion — Pre-Cut Tower / Drip-Loop Kit | Available on bulk export reels or pre-cut to turbine tower section and nacelle drip-loop lengths
| 1.8/3 (3.6) kV EPR/PCP Torsion — Cold Torsion & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, conductor DC resistance & cold-torsion qualification report

## Quality and supply
1.8/3 (3.6) kV 3GI3 EPR / LSOH & Polychloroprene Flexible Rubber Wind – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3-3-6-kv-flexible-rubber-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification) — DC resistance at 20 °C and insulation/sheath wall thickness within IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification limits | Every manufactured drum length
Routine test | AC high-voltage dielectric & insulation resistance test (IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification) — Zero dielectric breakdown and verified insulation resistance for 1.8/3 (3.6) kV rating | Every manufactured drum length
Type test | Low-temperature drip-loop torsion, oil & flame qualification (IEC 60502-1 & VDE 0207 3GI3 EPR Dynamic Wind Torsion Specification) — Verified cold torsion cycle endurance, oil resistance and flame retardancy across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | IEC 60502-1 / VDE 0250 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 1.8/3 (3.6) kV EPR/PCP Torsion IEC 60502-1 / VDE 0250 1.8/3 (3.6) kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel reels or pre-cut wind turbine tower & drip-loop kits
Supply | Standard lengths: 500 m, 1,000 m or custom cut-to-length nacelle drip-loop and tower section sets
Supply | MOQ: 100 m (standard configurations) · 300 m (custom wind builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP