## Request a quote
Request a quotation for 1.8/3 kV IEC / 2000V UL RHW-2 LSOH
Share governing standard (IEC/VDE/UL WTTC/GB/T), voltage rating (0.6/1 kV, 1.8/3 kV or 2,000 V), conductor (Cu or Al) × cross-section, torsion angle and drum length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/1-8-3kv-iec-2000v-ul-rhw-2-lsoh-torsion-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
Global Dual-Standard 1.8/3 (3.6) kV (IEC 60502-1) & 2,000 V (UL RHW-2 – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3kv-iec-2000v-ul-rhw-2-lsoh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Max. pulling kN ≈ | Min. bend R mm | Series
| 1.8/3 kV IEC / 2000V U 1×95 / 4G25 Cu | 1 × 95 mm² (or 4G25 mm² / 3/0 AWG) | IEC 60228 Class 5 Flexible Cu/SnCu | 21.6 | 1080 | 14.2 | 110 | 1.8/3 kV IEC / 2000V UL RHW-2 LSOH Construction Schedule (−40…+90 °C)
| 1.8/3 kV IEC / 2000V U 1×185 / 4G50 Cu | 1 × 185 mm² (or 4G50 mm² / 373 kcmil) | IEC 60228 Class 5 Flexible Cu/SnCu | 27.8 | 1960 | 27.5 | 140 | 1.8/3 kV IEC / 2000V UL RHW-2 LSOH Construction Schedule (−40…+90 °C)
| 1.8/3 kV IEC / 2000V U 1×300 / 4G95 Cu | 1 × 300 mm² (or 1×535/777 kcmil) | IEC 60228 Class 5 Flexible Cu/SnCu | 34.6 | 3120 | 45 | 175 | 1.8/3 kV IEC / 2000V UL RHW-2 LSOH Construction Schedule (−40…+90 °C)
Custom conductor cross-sections, core counts, pre-lugged tower kits and drum lengths available per IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification.

## Electrical & thermal parameters
Global Dual-Standard 1.8/3 (3.6) kV (IEC 60502-1) & 2,000 V (UL RHW-2 – Electrical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3kv-iec-2000v-ul-rhw-2-lsoh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ Ω/km | Rating / Impedance | Operating temp.
1 × 95 mm² (or 4G25 mm² / 3/0 AWG) | 0.206 | 1.8/3 kV / 2,000 V (320 A Cu) | −40…+90 °C
1 × 185 mm² (or 4G50 mm² / 373 kcmil) | 0.106 | 1.8/3 kV / 2,000 V (495 A Cu) | −40…+90 °C
1 × 300 mm² (or 1×535/777 kcmil) | 0.0641 | 1.8/3 kV / 2,000 V (680 A Cu) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, AC high-voltage spark/dielectric and dimensional verification.

## Technical data
Global Dual-Standard 1.8/3 (3.6) kV (IEC 60502-1) & 2,000 V (UL RHW-2 – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3kv-iec-2000v-ul-rhw-2-lsoh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.8/3 kV / 2,000 (Tested per IEC 60502-1 / UL 44 RHW-2)
Key data | Operating temp. | −40…+90 °C (Cold-climate & nacelle wind service)
Key data | Min. bend radius | 6 × OD (Drip-loop, hub & tower routing)
Key data | Core / conductor | Class 5 Annealed (IEC 60228 Class 5 flexible plain copper )
Key data | Outer protection | Black LSOH Therm (Low-smoke zero-halogen flame- and torsio)
Key data | Standard | IEC 60502-1 / UL (IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / U)
Electrical | Rated voltage / operating system | 1.8/3 kV / 2,000 V (IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification)
Electrical | Core / conductor construction | Class 5 Annealed Fine Copper (25-400 mm²) — IEC 60228 Class 5 flexible plain copper single-core conductor
Electrical | Primary dielectric / insulation | HEPR / EPR Dual-Standard Dielectric — Certified to both IEC 1.8/3 (3.6) kV and UL RHW-2 2,000 V
Thermal | Continuous operating temperature | −40…+90 °C (wind turbine nacelle, hub & tower duty)
Thermal | Low-temperature torsion & cold bend | Verified cold-flex and torsion endurance across −40…+90 °C per IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel cable drum
Mechanical | Outer jacket / sheath protection | Black LSOH Thermoset Elastomer Jacket — Low-smoke zero-halogen flame- and torsion-resistant outer sheath
Mechanical | Minimum bending radius | 6 × OD
Mechanical | Intermediate screen / separator / core layer | HEPR / EPR Dual-Standard Dielectric — Certified to both IEC 1.8/3 (3.6) kV and UL RHW-2 2,000 V
Resistance | Oil, grease, ozone & UV resistance | Resistant to wind turbine gearbox oil, hydraulic fluid, ozone and UV weathering per IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification
Resistance | Flame retardancy & smoke/halogen emission | Flame-retardant and environmental performance verified per IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification
Standards | Conductor & flame/test standards | IEC 60228 / IEC 60332-1-2 & -3 / UL 2277 WTTC / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | 1.8/3 kV IEC / 2000V UL RHW-2 LSOH
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Black LSOH Therm)
Identification | Customs tariff (HS) | 8544.49 / 8544.60

## Construction
Global Dual-Standard 1.8/3 (3.6) kV (IEC 60502-1) & 2,000 V (UL RHW-2 – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3kv-iec-2000v-ul-rhw-2-lsoh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 Annealed Fine Copper (25-400 mm² | IEC 60228 Class 5 flexible plain copper single-core conductor
2 | HEPR / EPR Dual-Standard Dielectric | Certified to both IEC 1.8/3 (3.6) kV and UL RHW-2 2,000 V
3 | Black LSOH Thermoset Elastomer Jacket | Low-smoke zero-halogen flame- and torsion-resistant outer sheath
| 1.8/3 kV IEC / 2000V UL RHW-2 LSOH — Standard Wind Turbine Execution | Built to IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification with class 5 annealed fine copper (25-400 mm²) and black lsoh thermoset elastomer jacket
| 1.8/3 kV IEC / 2000V UL RHW-2 LSOH — Pre-Cut Tower / Drip-Loop Kit | Available on bulk export reels or pre-cut to turbine tower section and nacelle drip-loop lengths
| 1.8/3 kV IEC / 2000V UL RHW-2 LSOH — Cold Torsion & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, conductor DC resistance & cold-torsion qualification report

## Quality and supply
Global Dual-Standard 1.8/3 (3.6) kV (IEC 60502-1) & 2,000 V (UL RHW-2 – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/1-8-3kv-iec-2000v-ul-rhw-2-lsoh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification) — DC resistance at 20 °C and insulation/sheath wall thickness within IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification limits | Every manufactured drum length
Routine test | AC high-voltage dielectric & insulation resistance test (IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification) — Zero dielectric breakdown and verified insulation resistance for 1.8/3 kV / 2,000 V rating | Every manufactured drum length
Type test | Low-temperature drip-loop torsion, oil & flame qualification (IEC 60502-1 (1.8/3 kV) & UL 44 RHW-2 / UL 2277 (2,000 V) Dual-Standard Wind Specification) — Verified cold torsion cycle endurance, oil resistance and flame retardancy across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | IEC 60502-1 / UL 44 RHW-2 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 1.8/3 kV IEC / 2000V UL RHW-2 LSOH IEC 60502-1 / UL 44 RHW-2 1.8/3 kV / 2,000 V CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel reels or pre-cut wind turbine tower & drip-loop kits
Supply | Standard lengths: 500 m, 1,000 m or custom cut-to-length nacelle drip-loop and tower section sets
Supply | MOQ: 100 m (standard configurations) · 300 m (custom wind builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP