## Request a quote
Request a quotation for 10-CHKCU / 22-CHKCU / 35-CHKCU
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for 10-CHKCU / 22-CHKCU / 35-CHKCU.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/chkcu-compact-substation-connection-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
10-CHKCU / 22-CHKCU / 35-CHKCU CHKCU Compact-Substation – Dimensions & weights (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/chkcu-compact-substation-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF C 33-226 / NF M 82-376 / IEC 60502-2 (10-CHKCU / 22-CHKCU / 35-CHKCU). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| 10-CHKCU 6/10 kV 1 × 35 mm² | 1 × 35 mm² (6/10 kV) | 35.0 mm² | 24.5 | 495 | 890 | 147 | Standard 10-CHKCU / 22-CHKCU / 35-CHKCU configurations
| 10-CHKCU 6/10 kV 1 × 95 mm² | 1 × 95 mm² (6/10 kV) | 95.0 mm² | 30.2 | 1110 | 1620 | 181 | Standard 10-CHKCU / 22-CHKCU / 35-CHKCU configurations
| 22-CHKCU 12/20 kV 1 × 35 mm² | 1 × 35 mm² (12/20 kV) | 35.0 mm² | 28.8 | 530 | 1160 | 173 | Standard 10-CHKCU / 22-CHKCU / 35-CHKCU configurations
| 22-CHKCU 12/20 kV 1 × 50 mm² | 1 × 50 mm² (12/20 kV) | 50.0 mm² | 30.5 | 685 | 1360 | 183 | Standard 10-CHKCU / 22-CHKCU / 35-CHKCU configurations
| 22-CHKCU 12/20 kV 1 × 95 mm² | 1 × 95 mm² (12/20 kV) | 95.0 mm² | 34.6 | 1150 | 1920 | 208 | Standard 10-CHKCU / 22-CHKCU / 35-CHKCU configurations
| 35-CHKCU 18/30 kV 1 × 95 mm² | 1 × 95 mm² (18/30 kV) | 95.0 mm² | 40.2 | 1220 | 2440 | 241 | Standard 10-CHKCU / 22-CHKCU / 35-CHKCU configurations
| 35-CHKCU 18/30 kV 1 × 150 mm² | 1 × 150 mm² (18/30 kV) | 150.0 mm² | 44 | 1790 | 3120 | 264 | Standard 10-CHKCU / 22-CHKCU / 35-CHKCU configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per NF C 33-226 / NF M 82-376 / IEC 60502-2 (10-CHKCU / 22-CHKCU / 35-CHKCU).

## Electrical & ampacity
10-CHKCU / 22-CHKCU / 35-CHKCU CHKCU Compact-Substation – Electrical & ampacity (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/chkcu-compact-substation-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF C 33-226 / NF M 82-376 / IEC 60502-2 (10-CHKCU / 22-CHKCU / 35-CHKCU). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
1 × 35 mm² (6/10 kV) | 0.565 | 198 | 178 | 5.01 | 1.12 | 21000
1 × 95 mm² (6/10 kV) | 0.21 | 365 | 328 | 13.59 | 0.43 | 21000
1 × 35 mm² (12/20 kV) | 0.565 | 198 | 178 | 5.01 | 1.12 | 42000
1 × 50 mm² (12/20 kV) | 0.393 | 245 | 220 | 7.15 | 0.81 | 42000
1 × 95 mm² (12/20 kV) | 0.21 | 365 | 328 | 13.59 | 0.43 | 42000
1 × 95 mm² (18/30 kV) | 0.21 | 365 | 328 | 13.59 | 0.43 | 63000
1 × 150 mm² (18/30 kV) | 0.132 | 480 | 432 | 21.45 | 0.29 | 63000
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per NF C 33-226 / NF M 82-376 / IEC 60502-2 (10-CHKCU / 22-CHKCU / 35-CHKCU).

## Technical data
10-CHKCU / 22-CHKCU / 35-CHKCU CHKCU Compact-Substation – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/chkcu-compact-substation-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF C 33-226 / NF M 82-376 / IEC 60502-2 (10-CHKCU / 22-CHKCU / 35-CHKCU). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage classes | 10 / 20 / 30 kV (6/10 kV, 12/20(24) kV, 18/30(36) kV)
Key data | Conductor | Class 5 Tinned (Flexible 16 mm² to 300 mm²)
Key data | HV insulation | 90 °C HV-EPR (Triple-extruded w/ semi-con screens)
Key data | Metallic screen | Tinned Cu Braid (Flexible copper braid / helically lapped)
Key data | Outer sheath | Heavy PCP / EM2 (Oil-, ozone- & flame-retardant neoprene)
Key data | Min. bend radius | 6 × D / 8 × D (Tight MV kiosk & transformer bays)
Electrical | Rated voltage U0/U (Um) | 10-CHKCU: 6/10(12) kV · 22-CHKCU: 12/20(24)
Electrical | Routine 5-min AC test voltage | 21 kV (10-CHKCU) · 42 kV (22-CHKCU) · 63 kV
Electrical | Partial discharge (PD) level | ≤ 10 pC at 1.73 × U0
Electrical | Max. conductor operating temp. | +90 °C continuous · +250 °C short-circuit
Electrical | Lightning impulse withstand | 75 kV (10-CHKCU) · 125 kV (22-CHKCU) · 170
Thermal | Operating temperature range | -25 °C to +80 °C ambient (-40 °C fixed
Thermal | Minimum installation temp. | -20 °C
Mechanical | Min. bending radius | 6 × D fixed inside substation kiosk · 10 ×
Mechanical | Max. tensile pulling load | 15 N/mm² of copper cross-section
Resistance | Oil & transformer fluid resistance | EN 60811-404 mineral oil & synthetic ester
Resistance | Flame & ozone resistance | IEC 60332-1-2 flame retardant · EN
Standards | Primary specification | NF M 82-376 / UTE C 33 / IEC 60502-2
Standards | Separable connector fit | Fits 250 A, 400 A & 630 A EN 50180 / EN
Identification | Core & screen | Peelable black outer semi-con under bright
Identification | Outer sheath colour | Black (with longitudinal voltage &

## Construction
10-CHKCU / 22-CHKCU / 35-CHKCU CHKCU Compact-Substation – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/chkcu-compact-substation-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF C 33-226 / NF M 82-376 / IEC 60502-2 (10-CHKCU / 22-CHKCU / 35-CHKCU). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 flexible tinned copper | IEC 60228 Class 5 flexible annealed tinned copper conductor (16 to 300 mm²) | IEC 60228 Class 5
2 | Triple-extruded Semi-Con + 90 °C HV-EPR | Inner semi-con elastomer + 90 °C high-modulus EPR (3.4 mm @ 10kV, 5.5 mm @ 20kV, 8.0 mm | NF M 82-376 / IEC 60502-2
3 | Flexible tinned copper metallic screen | Tinned copper wire braid or composite helical wires + counter-helix tape (≥ 16–25 mm²
4 | Separator tape | Non-woven / polyester binder tape over the copper screen | IEC 60502-2
5 | Heavy-duty polychloroprene (PCP) sheath | Cross-linked oil-, ozone-, weather-, and flame-retardant polychloroprene elastomer (Black) | EN 50363-2-1 EM2
| 10-CHKCU (6/10 kV, Um = 12 kV) & 22-CHKCU (12/20 kV, Um = 24 kV) | Standard 10 kV and 20 kV flexible single-core substation jumper cables (25 mm² to 240 mm²).
| 35-CHKCU (18/30 kV, Um = 36 kV) | 30/33 kV flexible single-core jumper cable for wind-farm collector substations and 33 kV mobile transformers.

## Quality and supply
10-CHKCU / 22-CHKCU / 35-CHKCU CHKCU Compact-Substation – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/chkcu-compact-substation-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF C 33-226 / NF M 82-376 / IEC 60502-2 (10-CHKCU / 22-CHKCU / 35-CHKCU). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Routine HV AC test (21 / 42 / 63 kV) & PD test — 5 min AC withstand; partial discharge ≤ 10 pC at 1.73 U0 | 100 % of drums
Routine test | Class 5 tinned Cu & metallic screen DC resistance — IEC 60228 Class 5 R20; screen fault capacity verification | 100 % of drums
Sample test | Outer semi-con peel force & HV-EPR hot-set — Clean cold-stripping for EN 50180/50181 separable connectors | Per production batch
Type test | BIL impulse + oil immersion + IEC 60332-1-2 flame — 75 / 125 / 170 kV impulse pass & EM2 oil resistance | Type approval
Standard / approval | NF M 82-376 / UTE C 33
Standard / approval | IEC 60502-2
Standard / approval | EN 50180 / EN 50181
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 10-CHKCU 6/10KV / 22-CHKCU
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP