## Request a quote
Request a quotation for 2XSEYQY 6/10 kV
Application engineer · MV mining & tunnel cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/xseyqy-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
2XSEYQY 6/10 kV XLPE-Insulated Steel-Braid Armoured Tunnel Cable – Dimensions & mechanical data (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/xseyqy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | OD min mm | OD max mm | Total weight ≈ kg/km | Min. bend R (fixed) mm | Max. pull (15 N/mm²) N
| 2XSEYQY 3 × 25/16 | 3 × 25/16 | 45 | 49.6 | 3650 | 496 | 1125
| 2XSEYQY 3 × 35/16 | 3 × 35/16 | 47.7 | 52.8 | 4200 | 528 | 1575
| 2XSEYQY 3 × 50/16 | 3 × 50/16 | 50.6 | 56 | 4960 | 560 | 2250
| 2XSEYQY 3 × 70/16 | 3 × 70/16 | 54.5 | 60.2 | 6030 | 602 | 3150
| 2XSEYQY 3 × 95/16 | 3 × 95/16 | 58.8 | 65 | 7300 | 650 | 4275
| 2XSEYQY 3 × 120/16 | 3 × 120/16 | 62 | 68.5 | 8410 | 685 | 5400
All sizes incorporate a 16 mm² copper tape screen over each core plus a ≥ 90 % coverage galvanized steel wire braid armour.

## Electrical parameters
2XSEYQY 6/10 kV XLPE-Insulated Steel-Braid Armoured Tunnel Cable – Electrical parameters (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/xseyqy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605 / IEC 60502-2. Values for your order are confirmed in the quotation.
Cores × mm² | Max. DC resistance at 20 °C Ω/km | Metallic screen | Current in air (30 °C) A | Routine AC test
3 × 25/16 | 0.727 | 16 mm² Cu tape / core | 131 | 17 kV AC
3 × 35/16 | 0.524 | 16 mm² Cu tape / core | 162 | 17 kV AC
3 × 50/16 | 0.387 | 16 mm² Cu tape / core | 196 | 17 kV AC
3 × 70/16 | 0.268 | 16 mm² Cu tape / core | 246 | 17 kV AC
3 × 95/16 | 0.193 | 16 mm² Cu tape / core | 298 | 17 kV AC
3 × 120/16 | 0.153 | 16 mm² Cu tape / core | 346 | 17 kV AC
Current ratings are typical values in free air at 30 °C ambient and 90 °C conductor temperature per IEC 60502-2.

## Technical data
2XSEYQY 6/10 kV XLPE-Insulated Steel-Braid Armoured Tunnel Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/xseyqy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 6/10 kV (Um = 12 kV · 17 kV AC test)
Key data | Core insulation | 2X (XLPE) (Compact low-loss XLPE (+90 °C))
Key data | Armour & screen | Cu + GSWB ≥ 90% (16 mm² Cu + steel braid)
Key data | Tensile load | 15 N/mm² (1,125 N to 5,400 N pull)
Key data | Torsion stress | ±25 °/m (Semi-mobile relocation)
Key data | Outer sheath | Red 5GM5 / FR (High-visibility MV red)
Electrical | Rated voltage U0/U (Um) | 6/10 kV (Um = 12 kV) per IEC 60502-2 / DIN VDE 0250-605
Electrical | AC test voltage | 17 kV AC routine dielectric test
Thermal | Ambient operating temperature | -25 to +60 °C flexible / relocation · -40 to +80 °C fixed installation
Thermal | Max. conductor temperature | +90 °C continuous operation · +250 °C short-circuit (max. 5 s)
Mechanical | Permissible tensile & torsional load | 15 N/mm² tensile load (1,125 N to 5,400 N) · ±25 °/m max. torsional stress
Mechanical | Min. bending radius | 15 × D during pulling / relocation · 10 × D fixed installation (DIN VDE 0298-3)
Standards | Reference standards | DIN VDE 0250-605 · IEC 60502-2 · DIN VDE 0295 / IEC 60228 Class 2 · DIN VDE 0207 (2XI1 XLPE)
Standards | Fire & environmental performance | Flame-retardant IEC 60332-1-2 · Oil-resistant IEC 60811-404 · Impact & crush resistant steel wire braid (≥ 90%)

## Construction
2XSEYQY 6/10 kV XLPE-Insulated Steel-Braid Armoured Tunnel Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/xseyqy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Conductors | Circular stranded bare copper, Class 2 per DIN VDE 0295 / IEC 60228 | 3 × 25 mm² to 3 × 120 mm² phase conductors
2 | Inner semi-conductive screen | Extruded semi-conductive cross-linked layer over each copper conductor | Smooths conductor surface field at 6/10 kV
3 | Core insulation (2X) | Cross-linked polyethylene (XLPE / 2XI1) dielectric compound
4 | Outer semi-conductive screen | Extruded semi-conductive layer over the XLPE core insulation
5 | Individual metallic core screen (SE) | Helically lapped bare copper tape screen over each phase core (16 mm² collective earth cross-section)
6 | Inner bedding sheath (Y) | Extruded PVC filler bedding over the three screened phase cores
7 | Galvanized steel wire braid armour (Q) | Braided galvanized steel wires with ≥ 90 % optical coverage
8 | Outer sheath (Y) | Heavy-duty flame-retardant special PVC / 5GM5 compound, high-visibility red
| 2XSEYQY 6/10 kV (3×25/16 – 3×120/16) | XLPE-insulated 6/10 kV (Um = 12 kV) 3-core tunnel feeder with 16 mm² copper screen and ≥ 90 % steel wire braid

## Quality and supply
2XSEYQY 6/10 kV XLPE-Insulated Steel-Braid Armoured Tunnel Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/xseyqy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | High-voltage AC dielectric test — 17 kV AC | Every drum length
Routine test | Partial discharge test — IEC 60502-2 / DIN VDE 0250-605 | Every drum length
Routine test | Conductor & screen DC resistance at 20 °C — IEC 60228 Class 2 | Every drum length
Sample test | Flame propagation — IEC 60332-1-2 | Per production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 2XSEYQY 6/10 kV [3×mm²/16] · DIN VDE 0250-605 · CE · [year] · [metre mark]
Supply | Standard packing: Heavy-duty steel or reinforced wooden drums for tunnel & mine transport
Supply | HS code: 8544.60
Supply | Minimum order: None
Supply | Lead time: None