## Request a quote
Request a quotation for 2XSLCYK-J
Application engineer · VFD & motor supply cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/xlpe-insulated-double-screened-vfd-motor-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
2XSLCYK-J XLPE-Insulated Double-Screened VFD Motor Cable – Dimensions & weights (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/xlpe-insulated-double-screened-vfd-motor-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0276-603 · IEC 60502-1 · EN 61800-3. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| 2XSLCYK-J 4G1.5 | 4G1.5 | 16 | 10.6 | 95 | 165 | 42 | 4G concentric (3 phase + 1 GNYE earth)
| 2XSLCYK-J 4G2.5 | 4G2.5 | 14 | 12.2 | 150 | 230 | 49 | 4G concentric (3 phase + 1 GNYE earth)
| 2XSLCYK-J 4G4 | 4G4 | 12 | 13.9 | 235 | 325 | 56 | 4G concentric (3 phase + 1 GNYE earth)
| 2XSLCYK-J 4G6 | 4G6 | 10 | 15.6 | 320 | 435 | 62 | 4G concentric (3 phase + 1 GNYE earth)
| 2XSLCYK-J 4G10 | 4G10 | 8 | 19.2 | 533 | 685 | 77 | 4G concentric (3 phase + 1 GNYE earth)
| 2XSLCYK-J 4G16 | 4G16 | 6 | 22.8 | 789 | 1010 | 91 | 4G concentric (3 phase + 1 GNYE earth)
| 2XSLCYK-J 3×16 + 3G2.5 | 3×16 + 3G2.5 | 6 | 21.4 | 662 | 895 | 86 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
| 2XSLCYK-J 3×25 + 3G4 | 3×25 + 3G4 | 4 | 25.2 | 1025 | 1310 | 101 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
| 2XSLCYK-J 3×35 + 3G6 | 3×35 + 3G6 | 2 | 28.4 | 1410 | 1740 | 114 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
| 2XSLCYK-J 3×50 + 3G10 | 3×50 + 3G10 | 1/0 | 32.8 | 2015 | 2430 | 131 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
| 2XSLCYK-J 3×70 + 3G10 | 3×70 + 3G10 | 2/0 | 37.2 | 2690 | 3180 | 149 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
| 2XSLCYK-J 3×95 + 3G16 | 3×95 + 3G16 | 3/0 | 42.6 | 3685 | 4290 | 170 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
| 2XSLCYK-J 3×120 + 3G16 | 3×120 + 3G16 | 4/0 | 46.8 | 4510 | 5180 | 187 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
| 2XSLCYK-J 3×150 + 3G25 | 3×150 + 3G25 | 300 kcmil | 51.9 | 5680 | 6490 | 208 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
| 2XSLCYK-J 3×185 + 3G35 | 3×185 + 3G35 | 350 kcmil | 57.4 | 7090 | 8050 | 230 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
| 2XSLCYK-J 3×240 + 3G50 | 3×240 + 3G50 | 500 kcmil | 64.2 | 9320 | 10480 | 257 | Symmetrical 3+3G (3 phase + 3 split GNYE earths)
Symmetrical 3+3G construction is recommended from 16 mm² upward to eliminate shaft voltages and common-mode bearing currents.

## Electrical & ampacity data
2XSLCYK-J XLPE-Insulated Double-Screened VFD Motor Cable – Electrical & ampacity data (15)
TEBAOFLEX ¦ https://tebaoflex.com/cables/xlpe-insulated-double-screened-vfd-motor-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0276-603 · IEC 60502-1 · EN 61800-3. Values for your order are confirmed in the quotation.
Phase conductor mm² | Max. DC R @ 20 °C Ω/km | C (core/core) pF/m ≈ | C (core/screen) pF/m ≈ | Inductance mH/km ≈ | Current rating +90 °C XLPE (A)
1.5 | 13.3 | 70 | 120 | 0.34 | 23
2.5 | 7.98 | 78 | 135 | 0.31 | 32
4 | 4.95 | 85 | 148 | 0.29 | 42
6 | 3.3 | 94 | 162 | 0.28 | 54
10 | 1.91 | 105 | 182 | 0.26 | 75
16 | 1.21 | 118 | 205 | 0.25 | 100
25 | 0.78 | 132 | 230 | 0.24 | 127
35 | 0.554 | 145 | 252 | 0.23 | 158
50 | 0.386 | 160 | 278 | 0.23 | 192
70 | 0.272 | 175 | 305 | 0.22 | 246
95 | 0.206 | 192 | 334 | 0.22 | 298
120 | 0.161 | 205 | 358 | 0.21 | 346
150 | 0.129 | 220 | 382 | 0.21 | 399
185 | 0.106 | 235 | 410 | 0.21 | 456
240 | 0.0801 | 252 | 440 | 0.2 | 538
XLPE (+90 °C) allows approx. 20–25 % higher continuous current capacity than PE (+70 °C) of identical cross-section.

## Technical data
2XSLCYK-J XLPE-Insulated Double-Screened VFD Motor Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/xlpe-insulated-double-screened-vfd-motor-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0276-603 · IEC 60502-1 · EN 61800-3. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (AC test voltage 4000 V)
Key data | EMC screening | Foil + ≥ 85% Cu (100% Al/PET tape + tinned Cu braid)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −40…+80 °C (fixed (−5…+70 °C flexing))
Key data | Min. bend radius | 4 × D fixed (15 × D occasional flexing)
Key data | Size range | 1.5–240 mm² (4G and symmetrical 3+3G)
Electrical | Rated voltage U0/U | 600/1000 V
Electrical | Max. operating voltage AC | 1200 V
Electrical | Max. operating voltage DC | 1800 V
Electrical | AC test voltage | 4000 V (5 min)
Electrical | Capacitance (core/core) | 70–252 pF/m (size dependent)
Electrical | Screen / Field control | 100% Al/PET tape + ≥ 85% tinned Cu braid
Electrical | Current rating | Per DIN VDE 0298-4 (+90 °C XLPE)
Thermal | Max. conductor temperature | +90 °C continuous
Thermal | Short-circuit temperature | +250 °C (max. 5 s)
Thermal | Temperature, fixed installation | −40 °C to +80 °C
Thermal | Temperature, flexing | −5 °C to +70 °C
Mechanical | Min. bending radius, fixed | 4 × OD
Mechanical | Min. bending radius, moving | 15 × OD (occasional flexing)
Mechanical | Max. tensile load (static) | 50 N/mm² (fixed) · 15 N/mm² (pulling)
Mechanical | Direct burial suitability | Yes, reinforced K-grade PVC sheath
Resistance | Flame retardance | IEC 60332-1-2 / EN 60332-1-2
Resistance | Oil resistance | Industrial oils & coolants (EN 50290-2-22)
Resistance | UV & ozone | UV-stabilised black PVC (ISO 4892-2)
Resistance | Water | AD7 / direct burial in damp ground
Standards | Cable type (construction standard) | DIN VDE 0276-603 / IEC 60502-1
Standards | Conductor | IEC 60228 / DIN EN 60228 Class 5
Standards | EMC compliance | EN 55011 / EN 61800-3
Standards | RoHS · REACH | 2011/65/EU (RoHS 2) & EC 1907/2006
Identification | Sheath colour | Black (RAL 9005), UV-resistant
Identification | Core identification | HD 308 S2 (brown, black, grey + GNYE)
Identification | Marking | TEBAOFLEX 2XSLCYK-J 0.6/1 kV [size] EMC CE
Identification | Customs tariff (HS) | 8544.49

## Construction
2XSLCYK-J XLPE-Insulated Double-Screened VFD Motor Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/xlpe-insulated-double-screened-vfd-motor-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0276-603 · IEC 60502-1 · EN 61800-3. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Conductor | Bare copper, finely stranded Class 5 | IEC 60228 / DIN EN 60228 Class 5
2 | Core insulation | Cross-linked polyethylene (XLPE, 2XI1), low capacitance | DIN VDE 0276-603 (+90 °C)
3 | Binding tape | Non-hygroscopic polyester wrapping tape over laid-up cores
4 | First EMC screen (foil) | Aluminium-laminated polyester tape (100 % coverage)
5 | Second EMC screen (braid) | Tinned copper wire braid (optical coverage ≥ 85 %) | Low transfer impedance ≤ 25 mΩ/m @ 30 MHz
6 | Outer sheath | Special black PVC compound (DMV6 / YMvK grade), UV & oil resistant | DIN VDE 0276-603 · direct burial capable
| 2XSLCYK-J 4G | Four concentric cores (1.5–16 mm²) with one green-yellow protective conductor
| 2XSLCYK-J 3+3G | Three phase cores plus three symmetrical interstitial earth cores (16–240 mm²)

## Quality and supply
2XSLCYK-J XLPE-Insulated Double-Screened VFD Motor Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/xlpe-insulated-double-screened-vfd-motor-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0276-603 · IEC 60502-1 · EN 61800-3. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage dielectric test — 4000 V AC for 5 min | Every manufactured drum length
Routine test | Conductor DC resistance check — Per IEC 60228 Class 5 limits at 20 °C | Every drum length
Sample test | Mutual capacitance & transfer impedance — Low pF/m & Zt ≤ 25 mΩ/m @ 30 MHz | Per production lot
Type test | Vertical flame propagation — Self-extinguishing per IEC 60332-1-2 | Type approval
Standard / approval | CE (2014/35/EU Low Voltage Directive)
Standard / approval | EN 61800-3 / EN 55011 EMC Class A/B
Standard / approval | IEC 60332-1-2 Flame Retardant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 2XSLCYK-J 0.6/1 kV [Cores×mm²] EMC LOW CAPACITANCE VFD MOTOR CABLE CE [Metre mark]
Supply | Delivery form: Cut-to-length or wooden export drums
Supply | Standard drum lengths: 500 m · 1000 m
Supply | MOQ: 100 m (stock sizes) · 500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP