## Request a quote
Request a quotation for 37-105VFD (MMV-VFD)
Application engineer · EMC & VFD drive cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/37-105vfd-mmv-vfd-8-15kv-symmetrical-shielded-medium-voltage-vfd-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
37-105VFD (MMV-VFD) 8/15 kV Symmetrical VFD Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/37-105vfd-mmv-vfd-8-15kv-symmetrical-shielded-medium-voltage-vfd-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on UL 1072 / IEEE 1580 / CSA C68.10. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| 37-105VFD 8 kV 3×1 AWG + 3×8 AWG(G) | 3×1 AWG + 3×8 AWG (G) | Extra-flex tinned Cu | 53.8 | 4120 | 19 | 430 | 37-105VFD (MMV-VFD) Construction Schedule (-40 to +90 °C)
| 37-105VFD 8 kV 3×2/0 AWG + 3×8 AWG(G) | 3×2/0 AWG + 3×8 AWG (G) | Extra-flex tinned Cu | 59.4 | 5360 | 26.8 | 475 | 37-105VFD (MMV-VFD) Construction Schedule (-40 to +90 °C)
| 37-105VFD 15 kV 3×4/0 AWG + 3×6 AWG(G) | 3×4/0 AWG + 3×6 AWG (G) | Extra-flex tinned Cu | 71.2 | 7890 | 42 | 570 | 37-105VFD (MMV-VFD) Construction Schedule (-40 to +90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per UL 1072 / IEEE 1580 / CSA C68.10.

## Electrical, optical & thermal p
37-105VFD (MMV-VFD) 8/15 kV Symmetrical VFD Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/37-105vfd-mmv-vfd-8-15kv-symmetrical-shielded-medium-voltage-vfd-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on UL 1072 / IEEE 1580 / CSA C68.10. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3×1 AWG + 3×8 AWG (8 kV) | 0.432 | 8 kV 133% (195 A) | -40 to +90 °C
3×2/0 AWG + 3×8 AWG (8 kV) | 0.272 | 8 kV 133% (260 A) | -40 to +90 °C
3×4/0 AWG + 3×6 AWG (15 kV) | 0.172 | 15 kV 133% (345 A) | -40 to +90 °C
Every production length undergoes routine conductor DC resistance, high-voltage Spark/AC dielectric or OTDR continuity and dimensional verification.

## Technical data
37-105VFD (MMV-VFD) 8/15 kV Symmetrical VFD Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/37-105vfd-mmv-vfd-8-15kv-symmetrical-shielded-medium-voltage-vfd-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on UL 1072 / IEEE 1580 / CSA C68.10. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 8/15 kV (8 kV / 15 kV (133% insulation level))
Key data | Operating temp. | -40 to +90 °C (Continuous mining & industrial duty)
Key data | Min. bend radius | 8 × OD (Fixed installation / dynamic routing)
Key data | Core / conductor | 3×2 AWG–4/0 AWG (Extra-flexible tinned Cu + 3 sym. ground)
Key data | Outer protection | Arctic Thermoset (Flame- & oil-resistant thermoset jacket)
Key data | Standard | UL 1072 (UL 1072 / IEEE 1580 / CSA C68.10)
Electrical | Rated voltage / transmission duty | 8/15 kV (UL 1072 / IEEE 1580 / CSA C68.10)
Electrical | Core / conductor construction | MV Phase Conductors (3×2/0 AWG) — Extra-flexible tinned copper + semicon shield + 133% 90 °C EPR insulation
Electrical | Primary dielectric / buffering | Individual Phase Shield — Strippable semicon layer + composite nylon & tinned copper braid (≥60%)
Thermal | Continuous operating temperature | -40 to +90 °C (mining & industrial service)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per UL 1072 / IEEE 1580 / CSA C68.10
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Arctic-Grade Outer Jacket (-J) — Flame-retardant, oil- and sunlight-resistant thermosetting outer jacket
Mechanical | Minimum bending radius | 8 × OD
Mechanical | Crush, impact & abrasion duty | Heavy-duty mining rock-cut, impact and tensile protection per UL 1072 / IEEE 1580 / CSA C68.10
Resistance | Flame retardancy & mine fire safety | Self-extinguishing / flame-retardant mining jacket per UL 1072 / IEEE 1580 / CSA C68.10
Resistance | Mine water, oil & chemical resistance | Resistant to acidic mine water, hydraulic oils and abrasion per UL 1072 / IEEE 1580 / CSA C68.10
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | UL 1072 / IEEE 1580 / CSA C68.10
Standards | Flame & environmental test standards | IEC 60332 / MSHA / EN 60794 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | 37-105VFD (MMV-VFD)
Identification | Sheath colour & metre marking | Continuous metre-marked black mining outer sheath
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
37-105VFD (MMV-VFD) 8/15 kV Symmetrical VFD Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/37-105vfd-mmv-vfd-8-15kv-symmetrical-shielded-medium-voltage-vfd-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on UL 1072 / IEEE 1580 / CSA C68.10. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | MV Phase Conductors (3×2/0 AWG) | Extra-flexible tinned copper + semicon shield + 133% 90 °C EPR insulation
2 | Individual Phase Shield | Strippable semicon layer + composite nylon & tinned copper braid (≥60%)
3 | Symmetrical Grounds (3×8 AWG XLPO) | Three green crosslinked polyolefin (XLPO) insulated flexible tinned copper grounds
4 | Isolation Jacket & Overall EMI Armor | Black XLPO inner jacket + tinned copper braid armor + 100% Al/PET tape
5 | Arctic-Grade Outer Jacket (-J) | Flame-retardant, oil- and sunlight-resistant thermosetting outer jacket
| 37-105VFD (MMV-VFD) — Standard Mining Execution | Built to UL 1072 / IEEE 1580 / CSA C68.10 with mv phase conductors (3×2/0 awg) and arctic-grade outer jacket (-j)
| 37-105VFD (MMV-VFD) — Custom Drum Length & Gland Kit | Available in custom shaft/roadway drum lengths or pre-terminated assemblies
| 37-105VFD (MMV-VFD) — Routine & Flame Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & flame test report

## Quality and supply
37-105VFD (MMV-VFD) 8/15 kV Symmetrical VFD Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/37-105vfd-mmv-vfd-8-15kv-symmetrical-shielded-medium-voltage-vfd-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on UL 1072 / IEEE 1580 / CSA C68.10. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (UL 1072 / IEEE 1580 / CSA C68.10) — DC resistance at 20 °C / optical attenuation and outer diameter within UL 1072 / IEEE 1580 / CSA C68.10 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (UL 1072 / IEEE 1580 / CSA C68.10) — Zero dielectric breakdown and verified insulation resistance over full production length | Every manufactured drum length
Type test | Flame propagation, mechanical crush & thermal ageing qualification (UL 1072 / IEEE 1580 / CSA C68.10) — Verified flame retardancy, mechanical integrity and thermal endurance across -40 to +90 °C | Type qualification & periodic lot audit
Standard / approval | UL 1072 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 37-105VFD (MMV-VFD) UL 1072 8/15 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel mine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shaft/reeling lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP