## Request a quote
Request a quotation for 3GSEGCH
Application engineer · marine & VFD cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/3gsegch-6-10kv-marine-offshore-emc-vfd-motor-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
3GSEGCH 6/10 kV Marine & Offshore EMC VFD Motor Cable – Dimensions, tensile ratings & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/3gsegch-6-10kv-marine-offshore-emc-vfd-motor-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60092-354 / IEC 60092-350. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Weight ≈ kg/km | Tensile load kN ≈ | Min. bend R mm | Series
| 3GSEGCH 3×35 mm² 6/10 kV | 3 × 35 mm² | Class 2 Cu + dual Cu screen | 41.5 | 2450 | 15.5 | 500 | 3GSEGCH Construction Schedule (−30…+90 °C)
| 3GSEGCH 3×50 mm² 6/10 kV | 3 × 50 mm² | Class 2 Cu + dual Cu screen | 44.8 | 3020 | 22 | 540 | 3GSEGCH Construction Schedule (−30…+90 °C)
| 3GSEGCH 3×70 mm² 6/10 kV | 3 × 70 mm² | Class 2 Cu + dual Cu screen | 48.6 | 3890 | 31 | 585 | 3GSEGCH Construction Schedule (−30…+90 °C)
| 3GSEGCH 3×95 mm² 6/10 kV | 3 × 95 mm² | Class 2 Cu + dual Cu screen | 52.8 | 4860 | 42 | 635 | 3GSEGCH Construction Schedule (−30…+90 °C)
| 3GSEGCH 3×120 mm² 6/10 kV | 3 × 120 mm² | Class 2 Cu + dual Cu screen | 56.4 | 5780 | 53 | 680 | 3GSEGCH Construction Schedule (−30…+90 °C)
Custom core counts, cross-sections, sheath colours and factory-tested cut lengths available per IEC 60092-354 / IEC 60092-350.

## Electrical, optical & thermal p
3GSEGCH 6/10 kV Marine & Offshore EMC VFD Motor Cable – Electrical, optical & thermal parameters (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/3gsegch-6-10kv-marine-offshore-emc-vfd-motor-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60092-354 / IEC 60092-350. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Capacity | Operating temp.
3 × 35 mm² | 0.524 | 6/10 kV / 155 A | −30…+90 °C
3 × 50 mm² | 0.387 | 6/10 kV / 190 A | −30…+90 °C
3 × 70 mm² | 0.268 | 6/10 kV / 235 A | −30…+90 °C
3 × 95 mm² | 0.193 | 6/10 kV / 285 A | −30…+90 °C
3 × 120 mm² | 0.153 | 6/10 kV / 330 A | −30…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric and dimensional verification.

## Technical data
3GSEGCH 6/10 kV Marine & Offshore EMC VFD Motor Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/3gsegch-6-10kv-marine-offshore-emc-vfd-motor-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60092-354 / IEC 60092-350. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 6/10 kV (3.6/6 kV PWM VFD motor duty)
Key data | Operating temp. | −30…+90 °C (Continuous thermal operating range)
Key data | Min. bend radius | 12–15 × OD (Installed / dynamic routing limit)
Key data | Core / conductor | Class 2 Cu (3-phase stranded plain copper)
Key data | Outer protection | SHF1 / ST8 LSZH (Red halogen-free marine sheath)
Key data | Standard | IEC 60092-354 (IEC 60092-354 / IEC 60092-350)
Electrical | Rated voltage / transmission duty | 6/10 kV (IEC 60092-354 / IEC 60092-350)
Electrical | Core / conductor construction | Phase Conductors (3x70 mm²) — Class 2 circular stranded plain annealed copper phase conductors for marine medium-voltage propulsion & VFD drives
Electrical | Primary dielectric / insulation | MV EPR Dielectric Stack — Triple-extruded inner semiconductive elastomer screen, 6/10 kV EPR primary dielectric, and outer semiconductive elastomer layer
Thermal | Continuous operating temperature | −30…+90 °C (rated operating envelope)
Thermal | Storage & transport temperature | −40…+80 °C on export drum or reel
Mechanical | Outer protection / sheath | Outer Sheath (ST8) — Red flame-retardant, low-smoke zero-halogen (LSZH / SHF1) polyolefin outer sheath for shipboard & offshore installations
Mechanical | Minimum bending radius | 12–15 × OD
Mechanical | Structural layer count | 6 concentric functional layers
Resistance | Environmental & chemical resistance | Industrial moisture, oils and mechanical wear per IEC 60092-354 / IEC 60092-350
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | IEC 60092-354 / IEC 60092-350
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | 3GSEGCH
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
3GSEGCH 6/10 kV Marine & Offshore EMC VFD Motor Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/3gsegch-6-10kv-marine-offshore-emc-vfd-motor-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60092-354 / IEC 60092-350. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase Conductors (3x70 mm²) | Class 2 circular stranded plain annealed copper phase conductors for marine medium-voltage propulsion & VFD drives | IEC 60092-354 / IEC 60092-350
2 | MV EPR Dielectric Stack | Triple-extruded inner semiconductive elastomer screen, 6/10 kV EPR primary dielectric, and outer semiconductive elastomer layer | IEC 60092-354 / IEC 60092-350
3 | Individual Phase Screen | Two overlapped helically lapped plain annealed copper tapes over each phase core for symmetrical radial field control | IEC 60092-354 / IEC 60092-350
4 | Inner Covering | Extruded black halogen-free flame-retardant elastomeric inner bedding filling core interstices | IEC 60092-354 / IEC 60092-350
5 | Overall Concentric EMC Screen | Helically served plain copper wires with a transverse copper counter-helix providing 100% EMC containment for PWM inverters | IEC 60092-354 / IEC 60092-350
6 | Outer Sheath (ST8) | Red flame-retardant, low-smoke zero-halogen (LSZH / SHF1) polyolefin outer sheath for shipboard & offshore installations | IEC 60092-354 / IEC 60092-350
| 3GSEGCH — Standard Execution | Built to IEC 60092-354 / IEC 60092-350 with phase conductors (3x70 mm²) and outer sheath (st8)
| 3GSEGCH — Custom Length & Configuration | Available in custom drum lengths, core counts or factory-terminated assemblies
| 3GSEGCH — Factory Routine Certified | Supplied with EN 10204 3.1 routine electrical, dielectric & dimensional inspection report

## Quality and supply
3GSEGCH 6/10 kV Marine & Offshore EMC VFD Motor Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/3gsegch-6-10kv-marine-offshore-emc-vfd-motor-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60092-354 / IEC 60092-350. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance & dimensional verification (IEC 60092-354 / IEC 60092-350) — Electrical parameters and outer diameter within IEC 60092-354 / IEC 60092-350 tolerances | Every manufactured drum / length
Routine test | High-voltage dielectric & insulation resistance test (IEC 60092-354 / IEC 60092-350) — Zero dielectric breakdown and verified insulation resistance over full length | Every manufactured drum / length
Type test | Thermal ageing, mechanical flexing & environmental qualification (IEC 60092-354 / IEC 60092-350) — Verified structural and dielectric integrity across −30…+90 °C | Type qualification & periodic lot audit
Standard / approval | IEC 60092-354 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 3GSEGCH IEC 60092-354 6/10 kV CE
Supply | Delivery form: Heavy-duty export wooden/steel drums or factory-tested coils
Supply | Standard lengths: 100 m, 250 m, 500 m, 1,000 m or custom cut-to-length reels
Supply | MOQ: 100 m (standard configurations) · 300 m (custom builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP