## Request a quote
Request a quotation for 400 Hz Aircraft Ground Power Cable
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/400-hz-aircraft-ground-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
400 Hz Aircraft Ground Power Cable – 400 Hz ratings, reactance & dimensions (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/400-hz-aircraft-ground-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SAE AS5756 / MIL-DTL-3432 / ISO 6858 / DFS 400. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | GPU cable rating | 6 Phase + 1 Neutral + Control | Outer Ø ≈ mm | Weight ≈ kg/m | 400 Hz Xʟ Ω/km | 400 Hz rating A (kVA) | Series
| 400Hz-90kVA (Metric 6×16+25) | 6×16 mm² Ph + 1×25 mm² N + 7×1.5C | 32.5 | 1.85 | 0.088 | 260 A (90 kVA) | 115/200 V 400 Hz Symmetrical 7-Power-Core + Control Cables
| 400Hz-140kVA (Metric 6×25+35) | 6×25 mm² Ph + 1×35 mm² N + 12×1.5C | 37.8 | 2.65 | 0.079 | 390 A (140 kVA) | 115/200 V 400 Hz Symmetrical 7-Power-Core + Control Cables
| 400Hz-180kVA (Metric 6×35+50) | 6×35 mm² Ph + 1×50 mm² N + 12×1.5C | 42.4 | 3.55 | 0.072 | 500 A (180 kVA) | 115/200 V 400 Hz Symmetrical 7-Power-Core + Control Cables
| 400Hz-180kVA (SAE 6×2AWG+1/0) | 6×2 AWG Ph + 1×1/0 AWG N + 6×16AWG | 41.8 | 3.42 | 0.074 | 500 A (180 kVA) | 115/200 V 400 Hz Symmetrical 7-Power-Core + Control Cables
At the ISO 461 aircraft nose plug, phase cores A1+A2 crimp into Pin A, B1+B2 into Pin B, and C1+C2 into Pin C.

## Technical data
400 Hz Aircraft Ground Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/400-hz-aircraft-ground-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SAE AS5756 / MIL-DTL-3432 / ISO 6858 / DFS 400. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | SAE AS5756 / ISO (600 V rating · 115/200 V 400 Hz)
Key data | Power geometry | 7-Core (6 Phase (2 parallel cores per phase around N)
Key data | 400 Hz reactance | ≤ 0.095 Ω/km (60 % lower ΔV than 4-core cable)
Key data | Control cores | 4 to 12 Cores (28 V DC E & F aircraft interlock)
Key data | Cold flexibility | -55 °C to +90 °C (Arctic apron & desert tarmac)
Key data | Outer jacket | Hi-Vis Yellow / (Skydrol, Jet-A & wheel crush)
Electrical | Operating system voltage | 115 / 200 V AC three-phase 400 Hz (cable insulation rated 600 V)
Electrical | 400 Hz inductive reactance | 0.068 to 0.092 Ω/km at 400 Hz (vs ~0.38 Ω/km for 4-core cable)
Electrical | 400 Hz voltage drop | 0.042–0.058 V / (A·km) at cos φ = 0.8 (400 Hz)
Electrical | Dielectric test voltage | 3,000 V AC on power cores · 1,500 V AC on control cores
Thermal | Continuous conductor temp. | +90 °C
Thermal | Dynamic apron temp. range | -55 °C to +80 °C (flexible operation on arctic/desert tarmacs)
Thermal | Short-circuit temperature | +250 °C
Mechanical | Nominal outer diameter | 32.5 mm (90 kVA) · 37.8 mm (140 kVA) · 42.5 mm (180 kVA)
Mechanical | Min. bend radius | 6 × OD (dynamic reeling / apron handling) · 4 × OD (static)
Mechanical | Wheel crush resistance | Withstands aircraft service truck and nose-gear tire roll-over
Resistance | Aviation fluid immunity | Resistant to Jet-A1 kerosene, Skydrol LD-4/500B hydraulic fluid & MIL-PRF-5606
Resistance | Runway de-icer & weather | Resistant to potassium/sodium formate, propylene glycol, UV & ozone
Resistance | Abrasion & flame | Concrete tarmac drag-resistant PUR/CPE · Flame retardant per IEC 60332-1-2
Standards | Aerospace GPU cable stds | SAE AS5756 · MIL-DTL-3432 · German DFS 400
Standards | Ground power interface | ISO 6858 & ISO 461 (6-pin + E/F interlock 400 Hz aircraft plug)
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Phase core identification | A1, B1, C1, A2, B2, C2 (paired at aircraft plug pins A, B, C) + Neutral N
Identification | Outer jacket colour | High-Visibility Safety Yellow (RAL 1021) or Aviation Orange (RAL 2009)
Identification | Customs tariff (HS) | 8544.4993

## Construction
400 Hz Aircraft Ground Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/400-hz-aircraft-ground-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SAE AS5756 / MIL-DTL-3432 / ISO 6858 / DFS 400. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Central Neutral + 6 Symmetrical Phase Conductors (Class 6 Cu) | 7 × extra-flexible rope-lay Class 6 (0.15–0.20 mm / 34–32 AWG) tinned or bare copper power cores: 1 central Neutral + 6 outer Phase cores (2 per phase: A1/A2, B1/B2, C1/C2)
2 | 4 to 12 × 28 V DC Interlock & Voltage-Sense Control Cores | 4, 6, 7 or 12 × 1.5–2.5 mm² (16–14 AWG) Class 6 tinned copper control cores laid around the central neutral or in outer interstices
3 | Low-loss 90 °C EPR / TPE-E dielectric insulation | High-flexibility ethylene propylene elastomer or thermoplastic polyester elastomer colour/number-coded A1, B1, C1, A2, B2, C2, N
4 | Anti-torsion synthetic yarn reinforcing braid | Open-weave high-tenacity polyamide/polyester anti-torsion braid embedded between inner and outer sheath layers
5 | Skydrol- & Jet-A-resistant Hi-Vis Yellow/Orange outer sheath | Heavy-duty cross-linked Chlorinated Polyethylene (CPE/PCP) or Polyether Polyurethane (PUR) in Safety Yellow (RAL 1021) or Orange
| 400Hz-90kVA (7 × 16 mm² / 6×6 AWG + 1×4 AWG + Control) | 90 kVA (260 A @ 400 Hz) lightweight stinger cable for regional jets, narrow-body aircraft (A320 / B737) and hangar pits
| 400Hz-140kVA (6 × 25 + 1 × 35 mm² + 6–12 Control) | 140 kVA (390 A @ 400 Hz) universal passenger boarding bridge reeling cable for narrow- and wide-body gates
| 400Hz-180kVA (6 × 35 + 1 × 50 mm² / 6×2 AWG + 1×1/0 AWG + Control) | 180 kVA (500 A @ 400 Hz) heavy-duty GPU cable for wide-body aircraft (B777 / B787 / A350 / A380 dual-plug)

## Quality and supply
400 Hz Aircraft Ground Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/400-hz-aircraft-ground-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SAE AS5756 / MIL-DTL-3432 / ISO 6858 / DFS 400. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 3.0 kV AC dielectric test, DC resistance & 400 Hz impedance verify — Zero breakdown and balanced 400 Hz phase reactance across A1/A2, B1/B2, C1/C2 | Every manufactured length
Type test | Skydrol LD-4, Jet-A1 & de-icer fluid immersion + -55 °C cold bend — Meets SAE AS5756 swell/tensile retention and zero cracking at -55 °C | Type qualification
Type test | Motorized boarding-bridge reel cyclic flexing & vehicle crush test — Zero core breakage or control-wire open circuit after cyclic reeling | Type qualification
Standard / approval | SAE AS5756 & MIL-DTL-3432
Standard / approval | ISO 6858 / ISO 461 Compatible
Standard / approval | DFS 400 German Airport Spec
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 400 HZ AIRCRAFT GROUND POWER CABLE SAE AS5756 / ISO 6858
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP