## Request a quote
Request a quotation for 74C068 SH C K1 SE NA
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/74c068-sh-c-k1-se-na-nuclear-k1-class-1e-control-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
74C068 SH C K1 SE NA Nuclear K1 Class 1E Control Cable – Dimensions & electrical ratings (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-c-k1-se-na-nuclear-k1-class-1e-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEEE 323 / IEEE 383 / IEC 60780-323. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × cross-section | Outer Ø ≈ mm | Weight ≈ kg/km | Max. DC R Ω/km | Min. bend R mm | Series
| 74C068 SH C K1 SE NA 2×1.5 | 2 × 1.5 mm² Screened | 10.6 | 165 | 12.2 | 85 | RCC-E K1 / Class 1E Screened Control Cables (0.6/1 kV)
| 74C068 SH C K1 SE NA 4×1.5 | 4 × 1.5 mm² Screened | 12.2 | 225 | 12.2 | 98 | RCC-E K1 / Class 1E Screened Control Cables (0.6/1 kV)
| 74C068 SH C K1 SE NA 7×1.5 | 7 × 1.5 mm² Screened | 14.4 | 325 | 12.2 | 115 | RCC-E K1 / Class 1E Screened Control Cables (0.6/1 kV)
| 74C068 SH C K1 SE NA 12×1.5 | 12 × 1.5 mm² Screened | 18.6 | 520 | 12.2 | 149 | RCC-E K1 / Class 1E Screened Control Cables (0.6/1 kV)
| 74C068 SH C K1 SE NA 4×2.5 | 4 × 2.5 mm² Screened | 13.8 | 295 | 7.56 | 110 | RCC-E K1 / Class 1E Screened Control Cables (0.6/1 kV)
| 74C068 SH C K1 SE NA 7×2.5 | 7 × 2.5 mm² Screened | 16.4 | 435 | 7.56 | 131 | RCC-E K1 / Class 1E Screened Control Cables (0.6/1 kV)
Supplied with full RCC-E / IEEE 323 batch traceability and ISO 19443 / NQA-1 certificate of conformance.

## Technical data
74C068 SH C K1 SE NA Nuclear K1 Class 1E Control Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-c-k1-se-na-nuclear-k1-class-1e-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEEE 323 / IEEE 383 / IEC 60780-323. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Qualification | RCC-E K1 / 1E (IEEE 323 / IEC 60780-323)
Key data | Voltage rating | 600/1000 V (4,000 V AC test voltage)
Key data | Radiation dose | ≥ 2.0 MGy (200 Mrad cumulative (normal+LOCA))
Key data | Design life | 60 years @ 55 °C (Arrhenius thermal aging qualified)
Key data | LOCA peak | +170 °C / 5.5 ba (Superheated steam + H₃BO₃/NaOH)
Key data | Conductor | 1.5 to 6.0 mm² (Tinned copper Class 2/5)
Electrical | Rated voltage (Uo/U) | 600 / 1000 V AC (0.6/1 kV)
Electrical | Max. DC resistance @ 20 °C | 12.2 Ω/km (1.5) · 7.56 Ω/km (2.5) · 4.70 Ω/km (4.0) · 3.11 Ω/km (6.0)
Electrical | AC dielectric test | 4,000 V rms for 5 min (routine) · 80 V/mil post-LOCA
Electrical | Insulation resistance | ≥ 1,500 MΩ·km @ 20 °C · ≥ 1.0 MΩ·km during LOCA peak
Thermal | Continuous operating temp. | -25 °C to +90 °C (60-year qualified life @ +55 °C)
Thermal | LOCA / HELB accident peak | +170 °C to +210 °C superheated steam @ 5.5 bar abs
Thermal | Short-circuit temperature | +250 °C (5 s)
Mechanical | Min. bend radius | 8 × OD (fixed) · 12 × OD (during pulling)
Mechanical | Seismic qualification | IEEE 344 / IEC 60980 OBE & SSE 6g triaxial response
Mechanical | Max. pulling tension | 50 N / mm² of total copper cross-section
Resistance | Gamma radiation resistance | ≥ 2.0 MGy (200 Mrad): 0.6 MGy aging + 1.4 MGy LOCA
Resistance | LOCA chemical spray | H₃BO₃ (3,000 ppm B) + NaOH / Na₂S₂O₃ spray pH 9.5–10.5
Resistance | Flame & halogen-free (SH) | IEEE 383 / IEC 60332-3-24 Cat C, IEC 60754-2 & IEC 61034-2
Standards | Nuclear qualification std | RCC-E (K1) · IEEE Std 323 · IEEE Std 383 · IEC 60780-323
Standards | Quality assurance | 10 CFR 50 Appendix B / ASME NQA-1 / ISO 19443
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Code breakdown | SH=Halogen-Free · C=Control · K1=In-Containment · SE=Overall Screen · NA=Unarmoured
Identification | Core identification | Black cores with White printed numbers (1, 2, 3...)
Identification | Customs tariff (HS) | 8544.4993

## Construction
74C068 SH C K1 SE NA Nuclear K1 Class 1E Control Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-c-k1-se-na-nuclear-k1-class-1e-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEEE 323 / IEEE 383 / IEC 60780-323. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned annealed copper conductors | Class 2 stranded or Class 5 flexible tinned copper per IEC 60228 (1.5, 2.5, 4.0, 6.0 mm²)
2 | Radiation-resistant K1 EPDM/EPR insulation | High-density radiation-cross-linked Ethylene Propylene Diene (EPDM/EPR) nuclear grade compound, numbered Black cores
3 | Halogen-free inner bedding & binder | Radiation-stable halogen-free elastomeric inner filling and polyester/mica separator tape
4 | Overall tinned copper braid screen (SE) | ≥ 85 % optical coverage tinned copper wire braid screen ('SE' = Sous Écran / Overall Screen) | Low transfer impedance ZT ≤ 50 mΩ/m @ 30 MHz
5 | SH Zero-Halogen K1 Cross-Linked Outer Sheath | Nuclear-grade Sans Halogène (SH) cross-linked polyolefin/elastomer outer jacket (Black or Blue)
| 74C068 SH C K1 SE NA (1.5 mm²) | 2 to 37 cores × 1.5 mm² overall braided Class 1E control cable for valve limits and solenoids
| 74C068 SH C K1 SE NA (2.5–6.0 mm²) | 2 to 19 cores × 2.5 / 4.0 / 6.0 mm² Class 1E control & feeder cable for actuators and heaters

## Quality and supply
74C068 SH C K1 SE NA Nuclear K1 Class 1E Control Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-c-k1-se-na-nuclear-k1-class-1e-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEEE 323 / IEEE 383 / IEC 60780-323. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 4.0 kV AC dielectric, IR & conductor resistance test — Zero breakdown for 5 min and IR ≥ 1,500 MΩ·km @ 20 °C | Every manufactured drum length
Type test | Sequential 60-year thermal aging + 2.0 MGy gamma + LOCA steam test — Passes 80 V/mil mandrel bend voltage test after full DBA/LOCA profile | K1 Type Qualification
Type test | IEEE 383 / IEC 60332-3-24 vertical tray flame test — Self-extinguishing with zero halogen acid gas (< 5 mg/g) | K1 Type Qualification
Standard / approval | RCC-E K1 & IEC 60780-323
Standard / approval | IEEE Std 323 & IEEE Std 383
Standard / approval | ISO 19443 / ASME NQA-1 QA
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 74C068 SH C K1 SE NA 0.6/1kV RCC-E K1 CLASS 1E
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP