## Request a quote
Request a quotation for 74C068 SH M K1 EG NA
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/74c068-sh-m-k1-eg-na-nuclear-k1-class-1e-measuring-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
74C068 SH M K1 EG NA Nuclear K1 Class 1E Measuring Cable – Dimensions & loop resistance (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-m-k1-eg-na-nuclear-k1-class-1e-measuring-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEEE 323 / IEEE 383 / IEC 60780-323. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Pairs × cross-section | Outer Ø ≈ mm | Weight ≈ kg/km | Max. DC R Ω/km | Min. bend R mm | Series
| 74C068 SH M K1 EG NA 1P×0.75 | 1 Pair × 0.75 mm² (EG) | 8.4 | 98 | 24.8 | 67 | RCC-E K1 / Class 1E Screened Measuring Cables
| 74C068 SH M K1 EG NA 1Q×0.75 | 1 Quad (4-wire RTD) × 0.75 mm² | 9.6 | 135 | 24.8 | 77 | RCC-E K1 / Class 1E Screened Measuring Cables
| 74C068 SH M K1 EG NA 2P×1.0 | 2 Pairs × 1.0 mm² (Indiv + EG) | 12.8 | 215 | 18.2 | 102 | RCC-E K1 / Class 1E Screened Measuring Cables
| 74C068 SH M K1 EG NA 4P×1.0 | 4 Pairs × 1.0 mm² (Indiv + EG) | 15.6 | 335 | 18.2 | 125 | RCC-E K1 / Class 1E Screened Measuring Cables
| 74C068 SH M K1 EG NA 7P×1.0 | 7 Pairs × 1.0 mm² (Indiv + EG) | 18.8 | 495 | 18.2 | 150 | RCC-E K1 / Class 1E Screened Measuring Cables
| 74C068 SH M K1 EG NA 12P×1.0 | 12 Pairs × 1.0 mm² (Indiv + EG) | 23.6 | 765 | 18.2 | 189 | RCC-E K1 / Class 1E Screened Measuring Cables
1-Quad (1Q) star-quad geometry provides balanced 4-wire Pt100 RTD resistance compensation.

## Technical data
74C068 SH M K1 EG NA Nuclear K1 Class 1E Measuring Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-m-k1-eg-na-nuclear-k1-class-1e-measuring-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEEE 323 / IEEE 383 / IEC 60780-323. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Qualification | RCC-E K1 / 1E (In-containment measuring)
Key data | Voltage rating | 150/250 V (300/500 V rated insulation)
Key data | Conductor | 0.50 to 1.5 mm² (Tinned copper twisted pairs)
Key data | Radiation dose | ≥ 2.0 MGy (60 yr + LOCA gamma dose)
Key data | Mutual cap. | ≤ 110 pF/m (Low signal distortion during DBA)
Key data | LOCA peak | +170 °C / 5.5 ba (High IR retention in steam)
Electrical | Rated voltage | 150/250 V (300/500 V peak insulation rating)
Electrical | Max. DC resistance @ 20 °C | 36.7 Ω/km (0.50) · 24.8 Ω/km (0.75) · 18.2 Ω/km (1.0) · 12.2 Ω/km (1.5)
Electrical | Insulation resistance @ 20 °C | ≥ 5,000 MΩ·km (normal) · ≥ 10 MΩ·km (@ +170 °C LOCA)
Electrical | Mutual capacitance | ≤ 110 pF/m @ 1 kHz
Thermal | Continuous operating temp. | -25 °C to +90 °C (60-year design life)
Thermal | LOCA / HELB accident peak | +170 °C to +210 °C saturated/superheated steam
Thermal | Short-circuit temperature | +250 °C (5 s)
Mechanical | Min. bend radius | 8 × OD (fixed) · 12 × OD (pulling)
Mechanical | Seismic qualification | IEEE 344 / IEC 60980 safe-shutdown earthquake (SSE)
Mechanical | Transfer impedance | ≤ 30 mΩ/m up to 30 MHz (EG dual screen)
Resistance | Gamma & beta radiation | ≥ 2.0 MGy (200 Mrad) cumulative dose
Resistance | Boric acid & alkaline spray | 30-day post-LOCA chemical spray & submergence
Resistance | Flame & smoke (SH) | IEEE 383 / IEC 60332-3-24, IEC 60754-2 & IEC 61034-2
Standards | Nuclear qualification | RCC-E K1 · IEEE 323 · IEEE 383 · RG 1.97 · IEC 60780-323
Standards | Quality program | ISO 19443 / ASME NQA-1 / 10 CFR 50 App B
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Code breakdown | SH=Halogen-Free · M=Mesure (Measuring) · K1=In-Containment · EG=Écran Général · NA=Unarmoured
Identification | Pair identification | Numbered Blue/White or Black/White twisted pairs
Identification | Customs tariff (HS) | 8544.4993

## Construction
74C068 SH M K1 EG NA Nuclear K1 Class 1E Measuring Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-m-k1-eg-na-nuclear-k1-class-1e-measuring-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEEE 323 / IEEE 383 / IEC 60780-323. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned annealed copper conductors | Class 2 (7-wire) or Class 5 tinned copper per IEC 60228 (0.50, 0.75, 0.93, 1.0, 1.5 mm²)
2 | High-IR K1 cross-linked EPDM / PEEK-EPR dielectric | Ultra-high-resistivity nuclear K1 elastomer formulated to minimize leakage current at +170 °C
3 | Individual pair screens (on multipair) | Tinned copper tape/braid or Al/PET screen with tinned drain wire over each twisted pair | ≥ 85 dB pair-to-pair crosstalk attenuation
4 | Écran Général (EG) overall EMC screen | Overall tinned copper wire braid (≥ 85 % coverage) + copper/PET tape barrier
5 | SH Zero-Halogen K1 Cross-Linked Outer Sheath | Radiation- and LOCA-resistant Sans Halogène (SH) cross-linked elastomer (Grey or Blue) | IEEE 383 & IEC 60332-3-24 flame retardant
| 74C068 SH M K1 EG NA (1 to 2 Pairs) | 1P or 2P × 0.75 / 1.0 mm² sensor drop cable for containment pressure transmitters and RTDs
| 74C068 SH M K1 EG NA (4 to 19 Pairs) | Individually + overall screened multipair trunk cable between containment junction boxes and penetrations

## Quality and supply
74C068 SH M K1 EG NA Nuclear K1 Class 1E Measuring Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-m-k1-eg-na-nuclear-k1-class-1e-measuring-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEEE 323 / IEEE 383 / IEC 60780-323. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 2.0 kV AC dielectric, IR (≥ 5 GΩ·km) & capacitance check — Zero breakdown and verified pair capacitance/crosstalk | Every manufactured drum length
Type test | LOCA Insulation Resistance (IR) & leakage current accuracy test — IR ≥ 10 MΩ·km at +170 °C steam so 4–20 mA error stays < 0.5 % | K1 Type Qualification
Type test | 2.0 MGy gamma irradiation + IEEE 383 vertical flame test — Pass post-LOCA mandrel bend and vertical tray burn | K1 Type Qualification
Standard / approval | RCC-E K1 & RG 1.97 Compliant
Standard / approval | IEEE Std 323 & IEEE Std 383
Standard / approval | ISO 19443 Nuclear QA
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 74C068 SH M K1 EG NA RCC-E K1 CLASS 1E MEASURING
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP