## Request a quote
Request a quotation for 74C068 SH MT K1 NA
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/74c068-sh-mt-k1-na-nuclear-k1-class-1e-thermocouple-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
74C068 SH MT K1 NA Nuclear K1 Class 1E Thermocouple Cable – Dimensions & loop resistance (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-mt-k1-na-nuclear-k1-class-1e-thermocouple-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEC 60584-3 / IEEE 323 / IEEE 383. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | TC type & pairs | Outer Ø ≈ mm | Weight ≈ kg/km | Loop R Ω/m | Min. bend R mm | Series
| 74C068 SH MT K1 NA 1P×1.0-KX | 1 Pair × 1.0 mm² Type KX (NiCr/NiAl) | 8.8 | 108 | 1.43 | 70 | RCC-E K1 / Class 1E Thermocouple Cables (IEC 60584-3 Class 1)
| 74C068 SH MT K1 NA 2P×1.0-KX | 2 Pairs × 1.0 mm² Type KX | 12.8 | 215 | 1.43 | 102 | RCC-E K1 / Class 1E Thermocouple Cables (IEC 60584-3 Class 1)
| 74C068 SH MT K1 NA 4P×1.0-KX | 4 Pairs × 1.0 mm² Type KX | 15.6 | 335 | 1.43 | 125 | RCC-E K1 / Class 1E Thermocouple Cables (IEC 60584-3 Class 1)
| 74C068 SH MT K1 NA 8P×1.0-KX | 8 Pairs × 1.0 mm² Type KX (CETM) | 19.8 | 540 | 1.43 | 158 | RCC-E K1 / Class 1E Thermocouple Cables (IEC 60584-3 Class 1)
| 74C068 SH MT K1 NA 12P×1.5-KX | 12 Pairs × 1.5 mm² Type KX (CETM) | 25.4 | 910 | 0.95 | 203 | RCC-E K1 / Class 1E Thermocouple Cables (IEC 60584-3 Class 1)
| 74C068 SH MT K1 NA 4P×1.0-NX | 4 Pairs × 1.0 mm² Type NX (Nicrosil/Nisil) | 15.6 | 335 | 1.72 | 125 | RCC-E K1 / Class 1E Thermocouple Cables (IEC 60584-3 Class 1)
Available in IEC 60584-3 (Green/Pink/Violet) or ANSI MC96.1 / ASTM E230 (Yellow/Orange/Purple) colour coding.

## Technical data
74C068 SH MT K1 NA Nuclear K1 Class 1E Thermocouple Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-mt-k1-na-nuclear-k1-class-1e-thermocouple-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEC 60584-3 / IEEE 323 / IEEE 383. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Qualification | RCC-E K1 / 1E (Mesure Thermocouple (MT))
Key data | TC calibration | Type K · N · E · (IEC 60584-3 Tolerance Class 1)
Key data | EMF tolerance | ±1.5 °C (Type K) (Special limits (±1.1 °C) opt.)
Key data | Radiation dose | ≥ 2.0 MGy (Zero EMF drift after 200 Mrad)
Key data | LOCA peak | +170 °C / 5.5 ba (High IR prevents EMF shunting)
Key data | Conductor | 0.50 to 1.5 mm² (Solid or 7-strand TC alloy)
Electrical | Thermocouple calibrations | Type K (KX/K) · Type N (NX/N) · Type E (EX/E) · Type J (JX/J)
Electrical | EMF accuracy class | IEC 60584-3 Class 1 (±1.5 °C) / ASTM E230 Special (±1.1 °C)
Electrical | Loop resistance @ 20 °C | ≈ 1.43 Ω/m (Type K 1.0 mm²) · ≈ 0.95 Ω/m (Type K 1.5 mm²)
Electrical | Insulation resistance | ≥ 5,000 MΩ·km @ 20 °C · ≥ 10 MΩ·km during +170 °C LOCA
Thermal | Continuous operating temp. | -25 °C to +90 °C (+150 °C extension calibration range)
Thermal | LOCA / HELB accident peak | +170 °C to +210 °C saturated/superheated steam
Thermal | 60-year thermal aging | Arrhenius-qualified for 60 years @ +55 °C containment ambient
Mechanical | Min. bend radius | 8 × OD (fixed) · 12 × OD (installation)
Mechanical | Seismic qualification | IEEE 344 / IEC 60980 OBE & SSE qualified
Mechanical | Conductor construction | Solid (Class 1) or 7-strand (Class 2) matched alloy
Resistance | Gamma radiation dose | ≥ 2.0 MGy (200 Mrad) without Seebeck EMF decalibration
Resistance | LOCA chemical spray | 30-day boric acid + NaOH spray & submergence pass
Resistance | Flame & halogen-free (SH) | IEEE 383 / IEC 60332-3-24, IEC 60754-2 & IEC 61034-2
Standards | Nuclear & TC standards | RCC-E K1 · IEC 60584-3 · IEEE 323 · IEEE 383 · RG 1.97
Standards | Quality assurance | ISO 19443 / ASME NQA-1 / 10 CFR 50 App B
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Code breakdown | SH=Halogen-Free · MT=Mesure Thermocouple · K1=In-Containment · NA=Unarmoured
Identification | Core colour code (IEC) | Type K: Green(+)/White(-) · Type N: Pink(+)/White(-) · Type E: Violet(+)/White(-)
Identification | Customs tariff (HS) | 8544.4993

## Construction
74C068 SH MT K1 NA Nuclear K1 Class 1E Thermocouple Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-mt-k1-na-nuclear-k1-class-1e-thermocouple-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEC 60584-3 / IEEE 323 / IEEE 383. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Matched thermocouple / extension alloy conductors | Solid (Class 1) or 7-strand (Class 2) IEC 60584-3 Class 1 alloys: Type K (NiCr/NiAl), Type N (NiCrSi/NiSi), Type E (NiCr/CuNi) or Type J (Fe/CuNi)
2 | High-IR K1 cross-linked EPDM dielectric | Radiation-cross-linked nuclear K1 elastomer with ultra-low ionic leachates
3 | Individual pair screens + matching TC drain | Aluminium/PET or copper/PET tape with tinned copper drain wire over each twisted thermocouple pair
4 | Overall tinned copper wire braid screen | ≥ 85 % optical coverage tinned copper braid screen | Common-mode EMI rejection ≥ 120 dB at 50/60 Hz
5 | SH Zero-Halogen K1 Cross-Linked Outer Sheath | Nuclear-grade Sans Halogène (SH) cross-linked elastomer (Green for Type K, Pink for Type N, Violet for Type E, or Black) | IEEE 383 & IEC 60332-3-24 compliant
| 74C068 SH MT K1 NA — Type KX/K (NiCr/NiAl) | 1 to 24 pairs × 0.5 / 1.0 / 1.5 mm² Type K Class 1 for PWR/EPR Core Exit Thermocouple Monitoring (CETM)
| 74C068 SH MT K1 NA — Type NX/N (Nicrosil/Nisil) | 1 to 12 pairs Type N Class 1 with enhanced nuclear transmutation and high-temp oxidation stability

## Quality and supply
74C068 SH MT K1 NA Nuclear K1 Class 1E Thermocouple Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-mt-k1-na-nuclear-k1-class-1e-thermocouple-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on RCC-E K1 / IEC 60584-3 / IEEE 323 / IEEE 383. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % Seebeck EMF calibration, 2.0 kV AC dielectric & IR test — EMF within IEC 60584-3 Class 1 (±1.5 °C) and IR ≥ 5,000 MΩ·km | Every manufactured drum length
Type test | LOCA +170 °C steam temperature error & IR retention test — Induced thermal-shunt EMF error < 1.0 °C during peak LOCA steam | K1 Type Qualification
Type test | 2.0 MGy gamma irradiation + IEEE 383 vertical flame test — Zero alloy decalibration and pass vertical tray flame burn | K1 Type Qualification
Standard / approval | RCC-E K1 & IEC 60584-3 Class 1
Standard / approval | IEEE Std 323 & IEEE Std 383
Standard / approval | ISO 19443 Nuclear QA
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 74C068 SH MT K1 NA TYPE KX CLASS 1 RCC-E K1
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP