## Request a quote
Request a quotation for 74C068 SH P K1 NA
Application engineer · nuclear Class 1E / K1 cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/74c068-sh-p-k1-na-nuclear-k1-class-1e-lv-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
74C068 SH P K1 NA Nuclear K1 Class 1E LV Power Cable – Dimensions, weights & ampacity (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-p-k1-na-nuclear-k1-class-1e-lv-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EDF CST 74C068 / RCC-E K1 / IEC 60780-323 / IEEE 323 & 383. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Voltage | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | In air 30 °C A | Min. bend R mm | Series
| 74C068 SH P K1 NA 2×2.5 | 2×2.5 mm² | 0.6/1 kV | 12 | 48 | 210 | 32 | 96 | Multi-Core 0.6/1 kV K1 Containment Power Feeders (74C068 SH P K1 NA)
| 74C068 SH P K1 NA 3G2.5 | 3G2.5 mm² | 0.6/1 kV | 12.6 | 72 | 238 | 28 | 101 | Multi-Core 0.6/1 kV K1 Containment Power Feeders (74C068 SH P K1 NA)
| 74C068 SH P K1 NA 3G4 | 3G4 mm² | 0.6/1 kV | 13.8 | 115 | 302 | 37 | 110 | Multi-Core 0.6/1 kV K1 Containment Power Feeders (74C068 SH P K1 NA)
| 74C068 SH P K1 NA 3G6 | 3G6 mm² | 0.6/1 kV | 15.1 | 173 | 385 | 48 | 121 | Multi-Core 0.6/1 kV K1 Containment Power Feeders (74C068 SH P K1 NA)
| 74C068 SH P K1 NA 3G10 | 3G10 mm² | 0.6/1 kV | 17.4 | 288 | 540 | 66 | 139 | Multi-Core 0.6/1 kV K1 Containment Power Feeders (74C068 SH P K1 NA)
| 74C068 SH P K1 NA 3G16 | 3G16 mm² | 0.6/1 kV | 19.8 | 461 | 760 | 88 | 158 | Multi-Core 0.6/1 kV K1 Containment Power Feeders (74C068 SH P K1 NA)
| 74C068 SH P K1 NA 3×25 | 3×25 mm² | 0.6/1 kV | 23.4 | 720 | 1120 | 117 | 187 | Multi-Core 0.6/1 kV K1 Containment Power Feeders (74C068 SH P K1 NA)
| 74C068 SH P K1 NA 3×50 | 3×50 mm² | 0.6/1 kV | 28.6 | 1440 | 1890 | 177 | 229 | Multi-Core 0.6/1 kV K1 Containment Power Feeders (74C068 SH P K1 NA)
| 74C068 SH P K1 NA 3×95 | 3×95 mm² | 0.6/1 kV | 36.2 | 2736 | 3280 | 268 | 290 | Multi-Core 0.6/1 kV K1 Containment Power Feeders (74C068 SH P K1 NA)
| 74C068 SH P K1 NA 1×120 | 1×120 mm² | 0.6/1 kV | 21.8 | 1152 | 1460 | 345 | 174 | Single-Core 0.6/1 kV K1 High-Current Motor & Bus Feeders
| 74C068 SH P K1 NA 1×185 | 1×185 mm² | 0.6/1 kV | 25.6 | 1776 | 2140 | 450 | 205 | Single-Core 0.6/1 kV K1 High-Current Motor & Bus Feeders
| 74C068 SH P K1 NA 1×240 | 1×240 mm² | 0.6/1 kV | 28.8 | 2304 | 2720 | 535 | 230 | Single-Core 0.6/1 kV K1 High-Current Motor & Bus Feeders
Screen-armoured (74C068 SH P K1 AR) and control/instrumentation (74C068 SH C / SH M K1) executions are also supplied.

## Technical data
74C068 SH P K1 NA Nuclear K1 Class 1E LV Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-p-k1-na-nuclear-k1-class-1e-lv-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EDF CST 74C068 / RCC-E K1 / IEC 60780-323 / IEEE 323 & 383. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Qualification | RCC-E K1 / 1E (inside reactor containment)
Key data | Rated voltage | 0.6/1 kV (Umax = 1.2 kV AC / 1.5 kV DC)
Key data | Design life | 60 Years @ 90 °C (Arrhenius thermal aging verified)
Key data | Radiation dose | ≥ 2,100 kGy (2.1 MGy (210 Mrad) LOCA + life)
Key data | LOCA steam | +175 °C / 5 bar (boric-acid & NaOH chemical spray)
Key data | Fire class | NF C 32-070 C1 (IEC 60332-3-22 Cat A · LSZH)
Electrical | Rated voltage (U₀/U) | 0.6/1 kV AC (Umax = 1.2 kV AC / 1.5 kV DC)
Electrical | Routine AC test voltage | 3.5 kV AC rms for 5 minutes
Electrical | Insulation resistance during LOCA peak | ≥ 1.0 MΩ·km at +175 °C saturated steam under 1,000 V energisation
Thermal | Normal continuous conductor temp. | +90 °C (qualified for 60-year service life at +55 °C containment ambient)
Thermal | LOCA / HELB accident peak temperature | +175 °C to +200 °C steam peak · +250 °C short-circuit (5 s)
Mechanical | Minimum bending radius | 8 × OD (fixed unarmoured NA) · 12 × OD (during pulling)
Mechanical | Post-LOCA mandrel bend test | Withstands 2.5 kV AC in water after 40 × OD coiled LOCA exposure
Resistance | Cumulative gamma radiation qualification | ≥ 2,100 kGy (850 kGy 60-yr aging + 1,250 kGy accident dose)
Resistance | Fire & halogen-free performance | NF C 32-070 C1, IEC 60332-3-22 Cat A, IEC 60754-1/2 & IEC 61034-2
Standards | Nuclear qualification standards | EDF CST 74C068, AFCEN RCC-E (K1), IEC 60780-323, IEEE 323 & IEEE 383
Standards | Quality assurance programme | ISO 19443 / ASME NQA-1 / RCC-E nuclear safety QA traceability
Identification | Designation code breakdown | 74C068 (EDF spec) + SH (LSZH) + P (Power) + K1 (Containment) + NA
Identification | Core identification | HD 308 S2 colour code or Black numbered 1, 2, 3… (+ G/Y on 'G' sizes)
Identification | Customs tariff (HS) | 8544.49

## Construction
74C068 SH P K1 NA Nuclear K1 Class 1E LV Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-p-k1-na-nuclear-k1-class-1e-lv-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EDF CST 74C068 / RCC-E K1 / IEC 60780-323 / IEEE 323 & 383. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded annealed bare copper (Class 2) | IEC 60228 / NF C 32-013 Class 2 stranded copper (1.5 to 300 mm²)
2 | Nuclear K1 radiation-resistant cross-linked EPR/EPDM | High-modulus Ethylene-Propylene elastomer formulated with anti-rad aromatic stabilizers
3 | Halogen-free fire-barrier inner bedding | Extruded non-hygroscopic LSZH elastomeric filler compound
4 | Cross-linked Sans Halogène (SH) K1 outer sheath | Thermoset Halogen-Free Flame-Retardant (HFFR) elastomer (Black with K1 identification
| 74C068 SH P K1 NA (Unarmoured Power) | SH (Sans Halogène) · P (Puissance / Power) · K1 (In-Containment) · NA (Non-Armé / Unarmoured)
| 74C068 SH P K1 AR (Armoured Option) | Adds galvanized steel tape/braid armour for exposed floor trenches

## Quality and supply
74C068 SH P K1 NA Nuclear K1 Class 1E LV Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/74c068-sh-p-k1-na-nuclear-k1-class-1e-lv-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EDF CST 74C068 / RCC-E K1 / IEC 60780-323 / IEEE 323 & 383. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Type test | Sequential 60-yr thermal aging + 2,100 kGy gamma + LOCA steam/spray test — Maintains rated voltage & IR ≥ 1 MΩ·km throughout 15-day LOCA profile | Qualification type test
Routine test | 3.5 kV AC 5-min dielectric & NF C 32-070 C1 flame test — Zero breakdown; char propagation within C1 / Cat A limits | Every batch
Standard / approval | AFCEN RCC-E Category K1 & EDF CST 74C068 Qualified
Standard / approval | IEC 60780-323 & IEEE 323 / IEEE 383 Class 1E
Standard / approval | NF C 32-070 C1 & IEC 60332-3-22 Cat A
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 74C068 SH P K1 NA 0.6/1kV <size> RCC-E K1 LOT#
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP