## Request a quote
Request a quotation for A-2Y(L)2YB2Y H45
Application engineer · control, railway, mining & tactical cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/a-2y-l-2yb2y-h45-low-capacitance-armoured-railway-telecom-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
A-2Y(L)2YB2Y H45 Low-Capacitance Armoured Railway Telecom Cable – Dimensions & weights (11)
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-2y-l-2yb2y-h45-low-capacitance-armoured-railway-telecom-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section / size | Conductor build | Wall ≈ mm | Outer Ø ≈ mm | Metal kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| A-2Y(L)2YB2Y 1×4×0.9 H45 | 1×4×0.9 | Solid / Stranded Cu | 1.43 | 13 | 99 | 225 | 195 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 2×4×0.9 H45 | 2×4×0.9 | Solid / Stranded Cu | 1.74 | 15.8 | 138.6 | 315 | 240 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 4×4×0.9 H45 | 4×4×0.9 | Solid / Stranded Cu | 1.98 | 18 | 187 | 425 | 270 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 6×4×0.9 H45 | 6×4×0.9 | Solid / Stranded Cu | 2.24 | 20.4 | 237.6 | 540 | 305 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 10×4×0.9 H45 | 10×4×0.9 | Solid / Stranded Cu | 2.6 | 23.6 | 323.4 | 735 | 355 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 20×4×0.9 H45 | 20×4×0.9 | Solid / Stranded Cu | 3.28 | 29.8 | 523.6 | 1190 | 450 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 1×4×1.2 H45 | 1×4×1.2 | Solid / Stranded Cu | 1.58 | 14.4 | 127.6 | 290 | 215 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 4×4×1.2 H45 | 4×4×1.2 | Solid / Stranded Cu | 2.22 | 20.2 | 255.2 | 580 | 305 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 1×4×1.4 H45 | 1×4×1.4 | Solid / Stranded Cu | 1.71 | 15.5 | 147.4 | 335 | 235 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 4×4×1.4 H45 | 4×4×1.4 | Solid / Stranded Cu | 2.4 | 21.8 | 305.8 | 695 | 330 | Standard A-2Y(L)2YB2Y H45 configurations
| A-2Y(L)2YB2Y 10×4×1.4 H45 | 10×4×1.4 | Solid / Stranded Cu | 3.26 | 29.6 | 589.6 | 1340 | 445 | Standard A-2Y(L)2YB2Y H45 configurations
Outer diameters and weights are nominal engineering values for A-2Y(L)2YB2Y H45 subject to standard manufacturing tolerances per DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification.

## Electrical & rating data
A-2Y(L)2YB2Y H45 Low-Capacitance Armoured Railway Telecom Cable – Electrical & rating data (11)
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-2y-l-2yb2y-h45-low-capacitance-armoured-railway-telecom-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Primary rating (A or nF/km) | Secondary rating | Dielectric test V AC rms
1×4×0.9 | 56.6 | 45 | 38.2 | 2500
2×4×0.9 | 56.6 | 45 | 38.2 | 2500
4×4×0.9 | 56.6 | 45 | 38.2 | 2500
6×4×0.9 | 56.6 | 45 | 38.2 | 2500
10×4×0.9 | 56.6 | 45 | 38.2 | 2500
20×4×0.9 | 56.6 | 45 | 38.2 | 2500
1×4×1.2 | 31.8 | 45 | 38.2 | 2500
4×4×1.2 | 31.8 | 45 | 38.2 | 2500
1×4×1.4 | 23.4 | 45 | 38.2 | 2500
4×4×1.4 | 23.4 | 45 | 38.2 | 2500
10×4×1.4 | 23.4 | 45 | 38.2 | 2500
Electrical resistance at +20 °C and dielectric withstand voltages verified per DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification.

## Technical data
A-2Y(L)2YB2Y H45 Low-Capacitance Armoured Railway Telecom Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-2y-l-2yb2y-h45-low-capacitance-armoured-railway-telecom-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Capacitance | H45 ≤ 45 nF/km (Low-loss at 800 Hz for axle counters)
Key data | Quad conductor | 0.9–1.4 mm Cu (Solid bare Cu star-quads (x4))
Key data | Barrier sheath | (L)2Y Al/PE (Bonded aluminum moisture barrier)
Key data | Armouring (B) | 2 × steel tape (Rodent & crush-resistant armour)
Key data | Test voltage | 2500 V AC (Core-to-core & core-to-screen)
Key data | Service temp. | -40…+70 °C (Trackside trough & direct burial)
Electrical | Mutual capacitance (H45) | ≤ 45 nF/km at 800 Hz
Electrical | Loop resistance (+20 °C) | ≤ 56.6 Ω/km (0.9) · ≤ 31.8 Ω/km (1.2) · ≤ 23.4 Ω/km (1.4)
Electrical | Insulation resistance | ≥ 5,000 MΩ·km at +20 °C
Electrical | AC dielectric test voltage | 2,500 V AC (core/core & core/screen)
Thermal | Operating temperature (fixed) | -40 °C to +70 °C
Thermal | Installation temperature | -20 °C to +50 °C
Mechanical | Quad construction | Low-capacitance star-quads (H45)
Mechanical | Armouring | Double galvanised steel tape ('B')
Mechanical | Min. bending radius | 15 × overall cable diameter
Mechanical | Max. pulling tension | 50 N/mm² of total copper area
Resistance | Moisture barrier | Al/PE laminated inner sheath (L)2Y
Resistance | Rodent & impact protection | Double steel tape armour ('B')
Resistance | UV & weather resistance | Carbon-black HDPE jacket (EN 50290-2-23)
Standards | Primary standards | DIN VDE 0816 & DB TL 416.0115 (H45)
Standards | RoHS & REACH | RoHS 3 & REACH compliant
Identification | Outer sheath colour | Black (RAL 9005)
Identification | Surface legend | TEBAOFLEX A-2Y(L)2YB2Y [n×4×d] H45 VDE 0816 [year]
Identification | Customs tariff (HS) | 8544.49

## Construction
A-2Y(L)2YB2Y H45 Low-Capacitance Armoured Railway Telecom Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-2y-l-2yb2y-h45-low-capacitance-armoured-railway-telecom-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid bare copper star-quads | Annealed solid bare copper wire (0.9 mm, 1.2 mm, or 1.4 mm) twisted into balanced star-quads
2 | H45 low-capacitance 2Y PE | Increased-wall low-density/cellular polyethylene (2Y) core insulation
3 | (L)2Y Al/PE laminated inner sheath | Longitudinally applied copolymer-coated aluminum tape fused to an extruded PE inner sheath
4 | Double steel tape armour (B) | Two helically lapped galvanised steel tapes over protective bedding
5 | 2Y black HDPE outer sheath | UV-resistant carbon-black polyethylene outer jacket
| A-2Y(L)2YB2Y n×4×0.9 H45 | 0.9 mm H45 (≤ 45 nF/km) star-quad cable for axle-counter heads and digital wayside modems
| A-2Y(L)2YB2Y n×4×1.2 / 1.4 H45 | 1.2 mm and 1.4 mm H45 star-quad cable for extended-reach axle counters and block signalling

## Quality and supply
A-2Y(L)2YB2Y H45 Low-Capacitance Armoured Railway Telecom Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-2y-l-2yb2y-h45-low-capacitance-armoured-railway-telecom-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Dielectric spark / high-voltage withstand test — 100 % in-line spark and AC/DC dielectric withstand per DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification | Every manufactured length
Routine test | Conductor DC resistance & continuity check — Within maximum 20 °C resistance limit specified for A-2Y(L)2YB2Y H45 | Every spool or drum length
Sample test | Insulation resistance & dimensional verification — Wall thickness, concentricity and insulation resistance per DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification | Per production batch
Type test | Environmental, mechanical & EMC qualification — Qualified to DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification thermal, mechanical and environmental performance criteria | Type qualification
Standard / approval | DIN VDE 0816 / DB 416.0115 H45 Low-Capacitance Axle-Counter & Telecom Specification
Standard / approval | CE (2014/35/EU) & RoHS 3 (2015/863/EU) Compliant
Standard / approval | REACH SVHC Compliance Verified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX A-2Y(L)2YB2Y 4x4x0.9 H45 VDE 0816 DB AXLE COUNTER
Supply | Delivery form: Export wooden drums, tactical reels or coils
Supply | Standard lengths: 100 m · 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP