## Request a quote
Request a quotation for A-H(L)HBH
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/a-h-l-hbh-lszh-armoured-outdoor-signalling-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
A-H(L)HBH LSZH Armoured Outdoor Signalling Cable – Dimensions & masses (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-h-l-hbh-lszh-armoured-outdoor-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / EN 50288-7. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Pairs × Ø / mm² | Cond. size | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| A-H(L)HBH 2×2×0.8 | 2×2×0.8 mm | 0.50 mm² | 11.8 | 19 | 210 | 142 | A-H(L)HBH standard series
| A-H(L)HBH 4×2×0.8 | 4×2×0.8 mm | 0.50 mm² | 13.2 | 39 | 265 | 158 | A-H(L)HBH standard series
| A-H(L)HBH 6×2×0.8 | 6×2×0.8 mm | 0.50 mm² | 14.8 | 58 | 330 | 178 | A-H(L)HBH standard series
| A-H(L)HBH 10×2×0.8 | 10×2×0.8 mm | 0.50 mm² | 16.9 | 96 | 435 | 203 | A-H(L)HBH standard series
| A-H(L)HBH 20×2×0.8 | 20×2×0.8 mm | 0.50 mm² | 20.5 | 193 | 660 | 246 | A-H(L)HBH standard series
| A-H(L)HBH 30×2×0.8 | 30×2×0.8 mm | 0.50 mm² | 23.8 | 289 | 890 | 286 | A-H(L)HBH standard series
| A-H(L)HBH 2×2×1.4 | 2×2×1.4 mm | 1.54 mm² | 14.5 | 59 | 315 | 174 | A-H(L)HBH standard series
| A-H(L)HBH 4×2×1.4 | 4×2×1.4 mm | 1.54 mm² | 16.8 | 118 | 430 | 202 | A-H(L)HBH standard series
| A-H(L)HBH 6×2×1.4 | 6×2×1.4 mm | 1.54 mm² | 19.2 | 177 | 565 | 230 | A-H(L)HBH standard series
| A-H(L)HBH 10×2×1.4 | 10×2×1.4 mm | 1.54 mm² | 22.4 | 296 | 810 | 269 | A-H(L)HBH standard series
| A-H(L)HBH 4×1.5 RE | 4×1.5 mm² | 1.50 mm² | 13.6 | 58 | 285 | 163 | A-H(L)HBH standard series
| A-H(L)HBH 7×1.5 RE | 7×1.5 mm² | 1.50 mm² | 15.4 | 101 | 365 | 185 | A-H(L)HBH standard series
| A-H(L)HBH 12×1.5 RE | 12×1.5 mm² | 1.50 mm² | 18.8 | 173 | 530 | 226 | A-H(L)HBH standard series
| A-H(L)HBH 4×2.5 RE | 4×2.5 mm² | 2.50 mm² | 14.9 | 96 | 350 | 179 | A-H(L)HBH standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per DIN VDE 0816 / EN 50288-7.

## Electrical data
A-H(L)HBH LSZH Armoured Outdoor Signalling Cable – Electrical data (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-h-l-hbh-lszh-armoured-outdoor-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / EN 50288-7. Values for your order are confirmed in the quotation.
Pairs × Ø / mm² | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
2×2×0.8 mm | 36.6 | 6 | 5
4×2×0.8 mm | 36.6 | 6 | 5
6×2×0.8 mm | 36.6 | 6 | 5
10×2×0.8 mm | 36.6 | 6 | 5
20×2×0.8 mm | 36.6 | 6 | 5
30×2×0.8 mm | 36.6 | 6 | 5
2×2×1.4 mm | 11.9 | 14 | 12
4×2×1.4 mm | 11.9 | 14 | 12
6×2×1.4 mm | 11.9 | 14 | 12
10×2×1.4 mm | 11.9 | 14 | 12
4×1.5 mm² | 12.1 | 18 | 15
7×1.5 mm² | 12.1 | 14 | 12
12×1.5 mm² | 12.1 | 11 | 9
4×2.5 mm² | 7.41 | 25 | 22
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
A-H(L)HBH LSZH Armoured Outdoor Signalling Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-h-l-hbh-lszh-armoured-outdoor-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / EN 50288-7. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Peak voltage | 300/500 V (Signalling, fire loop & telecom)
Key data | Water barrier | (L) Al-copolymer (Longitudinal moisture barrier + screen)
Key data | Armouring | 2 × steel tape ( (Helical galvanized steel tape armour)
Key data | Conductor | Solid Cu 0.8–1.4 (Or 0.5–2.5 mm² Class 1 copper)
Key data | Operating temp | -30 to +70 °C (Direct burial, tunnel & outdoor duct)
Key data | Min. bend radius | 12 × cable OD (Fixed armoured installation)
Electrical | Peak operating voltage | 300/500 V (telecom & signalling)
Electrical | Test voltage (core/core & core/screen) | 2000 V AC rms (50 Hz, 1 min)
Electrical | Mutual capacitance @ 800 Hz | ≤52 nF/km (0.8 mm star-quad)
Electrical | Insulation resistance | ≥5000 MΩ·km
Thermal | Operating temperature (fixed) | -30 °C to +70 °C
Thermal | Installation temperature | -5 °C to +50 °C
Mechanical | Minimum bend radius | 12 × cable outer diameter
Mechanical | Crush & rodent resistance | Double helical galvanized steel tape (2 × 0.15–0.20 mm)
Resistance | Bunched flame propagation | IEC 60332-3-24 Cat. C & IEC 60332-1-2
Resistance | Halogen-free & low smoke | IEC 60754-1/2 (pH ≥4.3) & IEC 61034-2 (≥60 % light transmission)
Resistance | Radial & longitudinal water block | Laminated sheath (L) per IEC 60794-1-22 Method F5
Standards | Design standard | DIN VDE 0816 / DIN VDE 0815 / EN 50288-7
Standards | Installation & fire code | DIN VDE 0891 & EN 50575 tunnel fire safety
Identification | Designation code | A = outdoor · H = halogen-free · (L)H = laminated sheath · B = steel tape armour · H = LSZH outer sheath
Identification | Outer sheath colour | Black (UV-stabilised outdoor/tunnel)

## Construction
A-H(L)HBH LSZH Armoured Outdoor Signalling Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-h-l-hbh-lszh-armoured-outdoor-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / EN 50288-7. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid bare copper conductor | Annealed solid bare copper wire (0.8 mm, 0.9 mm, 1.4 mm Ø or 0.75–2.5 mm²) per IEC 60228 Class 1 | IEC 60228
2 | Halogen-free polymer insulation (H) | Cross-linked or thermoplastic halogen-free compound with low mutual capacitance | DIN VDE 0816
3 | Water-swellable core wrapping | Non-hygroscopic dielectric and water-blocking swelling tapes over stranded pairs/quads | DIN VDE 0816
4 | Laminated Al-copolymer barrier (L) | Longitudinal aluminum tape copolymer-bonded to the halogen-free inner sheath H for radial moisture blocking & screening | DIN VDE 0816
5 | Double steel tape armour (B) | Two helically applied galvanized steel tapes providing rodent defense and magnetic screening | DIN VDE 0816
6 | Outer LSZH sheath (H) | UV-stabilised flame-retardant halogen-free polyolefin compound HM2/HM4 (Black or Grey) | DIN VDE 0816
| A-H(L)HBH n×2×0.8 (Star-Quad / Paired) | 0.8 mm solid copper telecom/fire-alarm signalling pairs for RS-485, Esserbus, Ringbus and voice evacuation trunks.
| A-H(L)HBH n×2×1.4 / n×1.5 mm² | Heavy-gauge 1.4 mm (1.5 mm²) conductors for long-distance railway axle counters, point machines and 24 VDC field power.

## Quality and supply
A-H(L)HBH LSZH Armoured Outdoor Signalling Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-h-l-hbh-lszh-armoured-outdoor-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / EN 50288-7. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 2.0 kV AC dielectric & spark test — No breakdown between cores and screen/armour for 1 min | 100 % of drums
Routine test | Loop resistance, capacitance & crosstalk — Meets DIN VDE 0816 star-quad attenuation and capacitance limits | 100 % of drums
Type test | IEC 60332-3-24 Cat. C flame & IEC 60754-2 halogen test — Passes vertical bunched flame and zero-halogen gas acidity | Type qualification
Standard / approval | DIN VDE 0816 / 0815
Standard / approval | IEC 60332-3-24 Cat. C
Standard / approval | IEC 60754-1/2 & IEC 61034-2
Standard / approval | RoHS 3 & CE Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX A-H(L)HBH 10x2x0.8 LG HAL-FREE IEC 60332-3-24 CE [year] [meter mark]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP