## Request a quote
Request a quotation for A-HHBH
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/a-hhbh-halogen-free-steel-tape-armoured-signalling-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
A-HHBH Halogen-Free Steel-Tape Armoured Signalling Cable – Dimensions & masses (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-hhbh-halogen-free-steel-tape-armoured-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DIN VDE 0276. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Configuration | Cond. size | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| A-HHBH 2×2×0.8 | 2×2×0.8 mm | 0.50 mm² | 11.2 | 19 | 195 | 134 | A-HHBH standard series
| A-HHBH 4×2×0.8 | 4×2×0.8 mm | 0.50 mm² | 12.6 | 39 | 250 | 151 | A-HHBH standard series
| A-HHBH 6×2×0.8 | 6×2×0.8 mm | 0.50 mm² | 14.2 | 58 | 310 | 170 | A-HHBH standard series
| A-HHBH 10×2×0.8 | 10×2×0.8 mm | 0.50 mm² | 16.2 | 96 | 410 | 194 | A-HHBH standard series
| A-HHBH 20×2×0.8 | 20×2×0.8 mm | 0.50 mm² | 19.8 | 193 | 625 | 238 | A-HHBH standard series
| A-HHBH 2×2×1.4 | 2×2×1.4 mm | 1.54 mm² | 13.8 | 59 | 295 | 166 | A-HHBH standard series
| A-HHBH 4×2×1.4 | 4×2×1.4 mm | 1.54 mm² | 16 | 118 | 405 | 192 | A-HHBH standard series
| A-HHBH 4×1.5 RE | 4×1.5 mm² | 1.50 mm² | 13 | 58 | 265 | 156 | A-HHBH standard series
| A-HHBH 7×1.5 RE | 7×1.5 mm² | 1.50 mm² | 14.8 | 101 | 345 | 178 | A-HHBH standard series
| A-HHBH 12×1.5 RE | 12×1.5 mm² | 1.50 mm² | 18 | 173 | 505 | 216 | A-HHBH standard series
| A-HHBH 19×1.5 RE | 19×1.5 mm² | 1.50 mm² | 20.6 | 274 | 690 | 247 | A-HHBH standard series
| A-HHBH 24×1.5 RE | 24×1.5 mm² | 1.50 mm² | 23.2 | 346 | 845 | 278 | A-HHBH standard series
| A-HHBH 4×2.5 RE | 4×2.5 mm² | 2.50 mm² | 14.2 | 96 | 330 | 170 | A-HHBH standard series
| A-HHBH 7×2.5 RE | 7×2.5 mm² | 2.50 mm² | 16.4 | 168 | 445 | 197 | A-HHBH standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per DIN VDE 0816 / DIN VDE 0276.

## Electrical data
A-HHBH Halogen-Free Steel-Tape Armoured Signalling Cable – Electrical data (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-hhbh-halogen-free-steel-tape-armoured-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DIN VDE 0276. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
2×2×0.8 mm | 36.6 | 6 | 5
4×2×0.8 mm | 36.6 | 6 | 5
6×2×0.8 mm | 36.6 | 6 | 5
10×2×0.8 mm | 36.6 | 6 | 5
20×2×0.8 mm | 36.6 | 6 | 5
2×2×1.4 mm | 11.9 | 14 | 12
4×2×1.4 mm | 11.9 | 14 | 12
4×1.5 mm² | 12.1 | 18 | 15
7×1.5 mm² | 12.1 | 14 | 12
12×1.5 mm² | 12.1 | 11 | 9
19×1.5 mm² | 12.1 | 9 | 8
24×1.5 mm² | 12.1 | 8 | 7
4×2.5 mm² | 7.41 | 25 | 22
7×2.5 mm² | 7.41 | 20 | 17
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
A-HHBH Halogen-Free Steel-Tape Armoured Signalling Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-hhbh-halogen-free-steel-tape-armoured-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DIN VDE 0276. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Peak voltage | 300/500 V (Signalling, control & fire alarm)
Key data | Armouring | 2 × steel tape ( (Galvanized steel tape rodent armour)
Key data | Conductor | Solid Cu Cl. 1 (0.8–1.4 mm Ø or 1.5–2.5 mm²)
Key data | Insulation & sheat | 100 % LSZH (H) (Core, inner bedding & outer jacket)
Key data | Operating temp | -30 to +70 °C (Outdoor duct, trench & tunnel)
Key data | Min. bend radius | 12 × cable OD (Fixed armoured routing)
Electrical | Rated voltage | 300/500 V
Electrical | Routine AC test voltage | 2000 V rms (50 Hz, 1 min)
Electrical | Insulation resistance @ 20 °C | ≥1000 MΩ·km
Thermal | Operating temperature range | -30 °C to +70 °C (up to +90 °C on cross-linked H grades)
Thermal | Min. installation temperature | -5 °C
Mechanical | Minimum bend radius | 12 × overall cable diameter
Mechanical | Impact & rodent resistance | Double helical galvanized steel tape armour
Resistance | Flame propagation | IEC 60332-3-24 Cat. C & EN 60332-1-2
Resistance | Halogen acidity & smoke | IEC 60754-1/2 (pH ≥4.3, ≤10 µS/mm) & IEC 61034-2 (≥60 % light transmittance)
Resistance | UV & outdoor weathering | Carbon-black UV-stabilised HM4 outer sheath
Standards | Reference standards | DIN VDE 0816 / DIN VDE 0815 / EN 50288-7
Standards | Installation standard | DIN VDE 0891 outdoor & tunnel routing
Identification | Code breakdown | A = outdoor · H = LSZH insulation · H = LSZH inner sheath · B = steel-tape armour · H = LSZH outer sheath
Identification | Outer sheath colour | Black (or Orange on fire-alarm special runs)

## Construction
A-HHBH Halogen-Free Steel-Tape Armoured Signalling Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-hhbh-halogen-free-steel-tape-armoured-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DIN VDE 0276. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid bare copper conductor | Annealed solid copper wire (0.8 mm, 1.4 mm Ø or 1.5–2.5 mm²) per IEC 60228 Class 1 | IEC 60228
2 | Halogen-free core insulation (H) | Cross-linked or thermoplastic zero-halogen compound | DIN VDE 0816
3 | Halogen-free inner sheath (H) | Extruded flame-retardant LSZH inner bedding under armour | DIN VDE 0816
4 | Double steel tape armour (B) | Two overlapping helical galvanized steel tapes (0.15–0.20 mm) for crush and rodent protection | DIN VDE 0816
5 | Outer LSZH sheath (H) | UV- and weather-resistant halogen-free polyolefin compound HM4, Black | DIN VDE 0816
| A-HHBH Paired / Star-Quad (0.8 / 1.4 mm) | Low-capacitance signalling pairs or star-quads for fire alarm ring buses, interlocks and railway telemetry.
| A-HHBH Multi-Core Control (1.5 / 2.5 mm²) | Numbered or colour-coded 1.5 mm² and 2.5 mm² control cores for outdoor damper actuators, hydrant valves and alarms.

## Quality and supply
A-HHBH Halogen-Free Steel-Tape Armoured Signalling Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/a-hhbh-halogen-free-steel-tape-armoured-signalling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0816 / DIN VDE 0276. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 2.0 kV AC dielectric test & conductor continuity — No breakdown at 2.0 kV rms for 1 minute | 100 % of drums
Type test | IEC 60332-3-24 Cat. C vertical bunched flame test — Charred portion ≤2.5 m above burner | Type qualification
Type test | IEC 60754-2 acid gas & IEC 61034-2 smoke density — pH ≥4.3, conductivity ≤10 µS/mm, transmittance ≥60 % | Type qualification
Standard / approval | DIN VDE 0816 / 0815
Standard / approval | IEC 60332-3-24 Cat. C
Standard / approval | IEC 60754-1/2 & IEC 61034-2
Standard / approval | RoHS 3 & CE Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX A-HHBH 7x1.5 RE HAL-FREE ARMOURED SIGNALLING IEC 60332-3-24 CE [year] [meter mark]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP