## Request a quote
Request a quotation for ACSS
Application engineer · overhead conductors & grid power
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/acss-aluminum-conductor-steel-supported/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
ACSS High-Temperature Overhead Conductor – Dimensions, stranding, breaking load & weights (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/acss-aluminum-conductor-steel-supported/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on ASTM B856 / IEC 62420. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Nominal area | Stranding | Outer Ø ≈ mm | Weight ≈ kg/km | Rated tensile kN ≈ | Min. sheave R mm | Series
| ACSS 50 mm² | 50 mm² | 7/3.00 mm | 9 | 138 | 14.5 | 180 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
| ACSS 95 mm² | 95 mm² | 19/2.52 mm | 12.6 | 262 | 28.2 | 252 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
| ACSS 120 mm² | 120 mm² | 19/2.85 mm | 14.3 | 334 | 36.4 | 286 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
| ACSS 150 mm² | 150 mm² | 26/2.70 + 7/2.10 | 17.1 | 546 | 53.8 | 342 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
| ACSS 185 mm² | 185 mm² | 26/3.00 + 7/2.33 | 19 | 674 | 65.2 | 380 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
| ACSS 240 mm² | 240 mm² | 26/3.44 + 7/2.68 | 21.8 | 885 | 84.5 | 436 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
| ACSS 300 mm² | 300 mm² | 26/3.86 + 7/3.00 | 24.5 | 1110 | 104.2 | 490 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
| ACSS 400 mm² | 400 mm² | 54/3.08 + 7/3.08 | 27.7 | 1432 | 126 | 554 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
| ACSS 500 mm² | 500 mm² | 54/3.44 + 7/3.44 | 31 | 1790 | 156.5 | 620 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
| ACSS 630 mm² | 630 mm² | 54/3.86 + 19/2.32 | 34.8 | 2245 | 194 | 696 | ACSS Standard Transmission & Distribution Schedule (−40…+200 °C)
Custom kcmil/code-word sizes, grease-filled corrosion protection and non-specular surface finishes available per ASTM B856 / IEC 62420.

## DC resistance & continuous curr
ACSS High-Temperature Overhead Conductor – DC resistance & continuous current ratings (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/acss-aluminum-conductor-steel-supported/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on ASTM B856 / IEC 62420. Values for your order are confirmed in the quotation.
Nominal area | Max. DC R₂₀ Ω/km | Continuous current A ≈ | Operating temp.
50 mm² | 0.578 | 210 | −40…+200 °C
95 mm² | 0.304 | 320 | −40…+200 °C
150 mm² | 0.192 | 435 | −40…+200 °C
240 mm² | 0.119 | 590 | −40…+200 °C
400 mm² | 0.072 | 820 | −40…+200 °C
630 mm² | 0.046 | 1080 | −40…+200 °C
Ampacity calculated per IEEE 738 (0.6 m/s wind, 40 °C ambient, 0.5 solar absorptivity / emissivity).

## Technical data
ACSS High-Temperature Overhead Conductor – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/acss-aluminum-conductor-steel-supported/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on ASTM B856 / IEC 62420. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | Up to 500 kV AC (Per ASTM B856 / IEC 62420)
Key data | Operating temp. | −40…+200 °C (Continuous thermal rating (ASTM B856))
Key data | Min. bend radius | 20 × OD (Installed / fixed routing)
Key data | Conductor | High-strength (7-wire or 19-wire high-tensile coated)
Key data | Outer layer | Fully annealed (Soft-annealed 1350-O aluminum wires)
Key data | Standard | ASTM B856 (ASTM B856 / IEC 62420)
Electrical | Rated voltage / duty | Up to 500 kV AC (ASTM B856 / IEC 62420)
Electrical | Conductor construction | High-strength galvanized / Galfan steel core — 7-wire or 19-wire high-tensile coated steel core supporting full mechanical tension
Electrical | Primary insulation / dielectric | Fully annealed 1350-O aluminum outer layers — Soft-annealed 1350-O aluminum wires (63 % IACS) rated to +200/+250 °C continuous
Thermal | Continuous operating temperature | −40…+200 °C per ASTM B856 / IEC 62420
Thermal | Short-circuit / peak thermal limit | +160 °C to +250 °C (5 s adiabatic limit depending on dielectric class)
Thermal | Minimum installation temperature | −5 °C (thermoplastic) / −25 °C (cross-linked or elastomer) / −40 °C (metallic)
Mechanical | Outer protection / covering | Fully annealed 1350-O aluminum outer layers — Soft-annealed 1350-O aluminum wires (63 % IACS) rated to +200/+250 °C continuous
Mechanical | Minimum bending radius | 20 × OD (installed / static routing)
Mechanical | Layer count & geometry | 2 concentric/structural layers verified by cross-section inspection
Resistance | Environmental & chemical durability | Engineered for industrial service in accordance with ASTM B856 / IEC 62420
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing product standard | ASTM B856 / IEC 62420
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | ACSS
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 7614.10

## Construction
ACSS High-Temperature Overhead Conductor – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/acss-aluminum-conductor-steel-supported/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on ASTM B856 / IEC 62420. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | High-strength galvanized / Galfan steel core | 7-wire or 19-wire high-tensile coated steel core supporting full mechanical tension | ASTM B856 / IEC 62420
2 | Fully annealed 1350-O aluminum outer layers | Soft-annealed 1350-O aluminum wires (63 % IACS) rated to +200/+250 °C continuous | ASTM B856 / IEC 62420
| ACSS — Standard Execution | Built to ASTM B856 / IEC 62420 with high-strength galvanized / galfan steel core and fully annealed 1350-o
| ACSS — Custom Cross-Sections | Full range of metric mm² and AWG/kcmil conductor sizes per ASTM B856 / IEC 62420
| ACSS — Export Drum Supply | Supplied with EN 10204 3.1 routine dielectric & conductor resistance test certificate

## Quality and supply
ACSS High-Temperature Overhead Conductor – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/acss-aluminum-conductor-steel-supported/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on ASTM B856 / IEC 62420. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (ASTM B856 / IEC 62420) — DC resistance at 20 °C and geometry within ASTM B856 / IEC 62420 class limits | Every manufactured drum / spool
Routine test | Routine dielectric / spark / structural integrity test (ASTM B856 / IEC 62420) — Zero breakdown or structural defect over full production length | Every manufactured drum / spool
Type test | Thermal aging, mechanical & material qualification (ASTM B856 / IEC 62420) — Full compliance with ASTM B856 / IEC 62420 across −40…+200 °C | Type qualification & periodic sample audit
Standard / approval | ASTM B856 Compliant
Standard / approval | EN 10204 3.1 Routine Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX ACSS <size> ASTM B856 Up to 500 kV AC CE
Supply | Delivery form: Non-returnable fumigated wooden drums or precision DIN spools
Supply | Standard lengths: 500 m · 1000 m · 2000 m drums (custom cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP