## Request a quote
Request a quotation for ARG7H1OR
Application engineer · MV power cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/arg7h1or-12-20kv-aluminium-hepr-screened-mv-power-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
ARG7H1OR 12/20 kV Aluminium HEPR Screened MV Power Cable – Dimensions, tensile ratings & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/arg7h1or-12-20kv-aluminium-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35755 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Weight ≈ kg/km | Tensile load kN ≈ | Min. bend R mm | Series
| ARG7H1OR 3×35 mm² 12/20 kV | 3 × 35 mm² Al | Class 2 compact Al + H1 screen | 46 | 1820 | 10.5 | 645 | ARG7H1OR Construction Schedule (−25…+90 °C)
| ARG7H1OR 3×50 mm² 12/20 kV | 3 × 50 mm² Al | Class 2 compact Al + H1 screen | 49 | 2090 | 15 | 690 | ARG7H1OR Construction Schedule (−25…+90 °C)
| ARG7H1OR 3×70 mm² 12/20 kV | 3 × 70 mm² Al | Class 2 compact Al + H1 screen | 53 | 2480 | 21 | 745 | ARG7H1OR Construction Schedule (−25…+90 °C)
| ARG7H1OR 3×95 mm² 12/20 kV | 3 × 95 mm² Al | Class 2 compact Al + H1 screen | 56.5 | 2910 | 28.5 | 790 | ARG7H1OR Construction Schedule (−25…+90 °C)
| ARG7H1OR 3×120 mm² 12/20 kV | 3 × 120 mm² Al | Class 2 compact Al + H1 screen | 60 | 3340 | 36 | 840 | ARG7H1OR Construction Schedule (−25…+90 °C)
Custom core counts, cross-sections, sheath colours and factory-tested cut lengths available per CEI UNEL 35755 / IEC 60502-2.

## Electrical, optical & thermal p
ARG7H1OR 12/20 kV Aluminium HEPR Screened MV Power Cable – Electrical, optical & thermal parameters (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/arg7h1or-12-20kv-aluminium-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35755 / IEC 60502-2. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Capacity | Operating temp.
3 × 35 mm² Al | 0.868 | 12/20 kV / 135 A | −25…+90 °C
3 × 50 mm² Al | 0.641 | 12/20 kV / 162 A | −25…+90 °C
3 × 70 mm² Al | 0.443 | 12/20 kV / 200 A | −25…+90 °C
3 × 95 mm² Al | 0.32 | 12/20 kV / 242 A | −25…+90 °C
3 × 120 mm² Al | 0.253 | 12/20 kV / 278 A | −25…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric and dimensional verification.

## Technical data
ARG7H1OR 12/20 kV Aluminium HEPR Screened MV Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/arg7h1or-12-20kv-aluminium-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35755 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 12/20 (24) kV (Three-phase MV distribution)
Key data | Operating temp. | −25…+90 °C (Continuous thermal operating range)
Key data | Min. bend radius | 14 × OD (Installed / dynamic routing limit)
Key data | Core / conductor | Class 2 Al (3×compact stranded aluminium)
Key data | Outer protection | Red Rz PVC (Flame-retardant OR outer jacket)
Key data | Standard | CEI UNEL 35755 (CEI UNEL 35755 / IEC 60502-2)
Electrical | Rated voltage / transmission duty | 12/20 (24) kV (CEI UNEL 35755 / IEC 60502-2)
Electrical | Core / conductor construction | Aluminium Conductors (3x50 mm²) — Class 2 compact circular stranded aluminium alloy conductors (Code A) for medium-voltage distribution networks
Electrical | Primary dielectric / insulation | Triple-Extruded Core Stack — Simultaneously extruded inner semiconductive screen, high-modulus G7 HEPR insulation (105 °C rated), and strippable outer semicon
Thermal | Continuous operating temperature | −25…+90 °C (rated operating envelope)
Thermal | Storage & transport temperature | −40…+80 °C on export drum or reel
Mechanical | Outer protection / sheath | Common Outer Sheath (OR) — Abrasion- and flame-retardant red Rz polyvinyl chloride (PVC) overall outer jacket
Mechanical | Minimum bending radius | 14 × OD
Mechanical | Structural layer count | 5 concentric functional layers
Resistance | Environmental & chemical resistance | Industrial moisture, oils and mechanical wear per CEI UNEL 35755 / IEC 60502-2
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | CEI UNEL 35755 / IEC 60502-2
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | ARG7H1OR
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
ARG7H1OR 12/20 kV Aluminium HEPR Screened MV Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/arg7h1or-12-20kv-aluminium-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35755 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Aluminium Conductors (3x50 mm²) | Class 2 compact circular stranded aluminium alloy conductors (Code A) for medium-voltage distribution networks | CEI UNEL 35755 / IEC 60502-2
2 | Triple-Extruded Core Stack | Simultaneously extruded inner semiconductive screen, high-modulus G7 HEPR insulation (105 °C rated), and strippable outer semicon | CEI UNEL 35755 / IEC 60502-2
3 | Individual Phase Screen (H1) | Helically lapped plain annealed copper tape applied over each phase core for earth-fault current return | CEI UNEL 35755 / IEC 60502-2
4 | Interstitial Filler Bedding | Extruded non-hygroscopic polymeric filler compound stabilizing the three-core lay | CEI UNEL 35755 / IEC 60502-2
5 | Common Outer Sheath (OR) | Abrasion- and flame-retardant red Rz polyvinyl chloride (PVC) overall outer jacket | CEI UNEL 35755 / IEC 60502-2
| ARG7H1OR — Standard Execution | Built to CEI UNEL 35755 / IEC 60502-2 with aluminium conductors (3x50 mm²) and common outer sheath (or)
| ARG7H1OR — Custom Length & Configuration | Available in custom drum lengths, core counts or factory-terminated assemblies
| ARG7H1OR — Factory Routine Certified | Supplied with EN 10204 3.1 routine electrical, dielectric & dimensional inspection report

## Quality and supply
ARG7H1OR 12/20 kV Aluminium HEPR Screened MV Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/arg7h1or-12-20kv-aluminium-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35755 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance & dimensional verification (CEI UNEL 35755 / IEC 60502-2) — Electrical parameters and outer diameter within CEI UNEL 35755 / IEC 60502-2 tolerances | Every manufactured drum / length
Routine test | High-voltage dielectric & insulation resistance test (CEI UNEL 35755 / IEC 60502-2) — Zero dielectric breakdown and verified insulation resistance over full length | Every manufactured drum / length
Type test | Thermal ageing, mechanical flexing & environmental qualification (CEI UNEL 35755 / IEC 60502-2) — Verified structural and dielectric integrity across −25…+90 °C | Type qualification & periodic lot audit
Standard / approval | CEI UNEL 35755 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX ARG7H1OR CEI UNEL 35755 12/20 (24) kV CE
Supply | Delivery form: Heavy-duty export wooden/steel drums or factory-tested coils
Supply | Standard lengths: 100 m, 250 m, 500 m, 1,000 m or custom cut-to-length reels
Supply | MOQ: 100 m (standard configurations) · 300 m (custom builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP