## Request a quote
Request a quotation for AS/NZS 1802
Specify the AS/NZS 1802 type code (209, 210, 240, 241, 241SF, 241 Superflex, 245, 245UF, 260 or 275), voltage grade (1.1 to 11 kV), conductor size (mm²) and machine duty (longwall shearer chain, continuous miner, shuttle car or monorail).
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/as-nzs-1802-underground-mining-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
AS/NZS 1802 Underground Coal Mining Reeling & Trailing Cables – Dimensions & mass (255) (255)
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1802-underground-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1802. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Type · grade · size | Voltage U0/U | Phase area (mm²) | Conductor Ø (mm) | R-EP-90 wall (mm) | Screen / earth (mm²) | Outer sheath (mm) | Nominal OD (mm) | Total mass (kg/km) | Series
| Type 209.1 · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 10 | 4.6 | 1.5 | 8.2 | 3.8 | 33.3 | 1750 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 | 6.2 | 1.6 | 10 | 4 | 37.3 | 2250 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 | 7.2 | 1.6 | 12 | 4.3 | 40.3 | 2850 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 | 8.4 | 1.6 | 14 | 4.6 | 43.6 | 3350 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 9.7 | 1.7 | 14 | 5 | 47.7 | 4100 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 12 | 1.8 | 16 | 5.4 | 54 | 5400 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 13.3 | 2 | 18 | 6 | 58.9 | 6450 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 15.3 | 2.1 | 21 | 6.4 | 64.6 | 7900 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 17.2 | 2.3 | 23 | 6.9 | 70.4 | 9550 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 | 18.8 | 2.5 | 30 | 7.4 | 76.5 | 11550 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 | 21.7 | 2.8 | 34 | 8.2 | 85.5 | 14450 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.1 · 1.1/1.1 kV · 3×300 mm² | 1.1/1.1 kV | 300 | 24.3 | 3 | 49 | 8.8 | 94.3 | 17900 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×16 mm² | 3.3/3.3 kV | 16 | 6.2 | 3 | 14 | 5.3 | 47.3 | 3350 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×25 mm² | 3.3/3.3 kV | 25 | 7.2 | 3 | 15 | 5.6 | 50.4 | 4000 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×35 mm² | 3.3/3.3 kV | 35 | 8.4 | 3 | 16 | 5.9 | 53.5 | 4600 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 | 9.7 | 3 | 17 | 6.3 | 57.2 | 5400 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 12 | 3 | 19 | 6.6 | 62.6 | 6650 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 13.3 | 3 | 21 | 7.1 | 66.4 | 7650 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 15.3 | 3 | 27 | 7.4 | 72 | 9300 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 17.2 | 3 | 32 | 7.8 | 76.7 | 10950 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 | 18.8 | 3 | 42 | 8.2 | 82.3 | 12850 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 | 21.7 | 3 | 48 | 8.8 | 89.6 | 15550 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.3 · 3.3/3.3 kV · 3×300 mm² | 3.3/3.3 kV | 300 | 24.3 | 3 | 63 | 9.4 | 97.7 | 19000 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×16 mm² | 6.6/6.6 kV | 16 | 6.2 | 5 | 17 | 6.4 | 58.2 | 4750 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×25 mm² | 6.6/6.6 kV | 25 | 7.2 | 5 | 19 | 6.7 | 61.7 | 5600 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×35 mm² | 6.6/6.6 kV | 35 | 8.4 | 5 | 21 | 7 | 64.8 | 6300 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×50 mm² | 6.6/6.6 kV | 50 | 9.7 | 5 | 22 | 7.3 | 68.2 | 7150 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 | 12 | 5 | 23 | 7.7 | 73.8 | 8600 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 | 13.3 | 5 | 30 | 8.1 | 78 | 9950 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 | 15.3 | 5 | 32 | 8.5 | 83.2 | 11550 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 | 17.2 | 5 | 46 | 8.9 | 89.2 | 13700 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 | 18.8 | 5 | 48 | 9.3 | 93.3 | 15400 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 | 21.7 | 5 | 53 | 9.9 | 101 | 18250 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.6 · 6.6/6.6 kV · 3×300 mm² | 6.6/6.6 kV | 300 | 24.3 | 5 | 71 | 10.4 | 109 | 21950 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.11 · 11/11 kV · 3×25 mm² | 11/11 kV | 25 | 7.2 | 7.6 | 24 | 8.1 | 75.9 | 8050 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.11 · 11/11 kV · 3×35 mm² | 11/11 kV | 35 | 8.4 | 7.6 | 30 | 8.4 | 79.6 | 9150 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.11 · 11/11 kV · 3×50 mm² | 11/11 kV | 50 | 9.7 | 7.6 | 32 | 8.7 | 83 | 10100 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.11 · 11/11 kV · 3×70 mm² | 11/11 kV | 70 | 12 | 7.6 | 35 | 9.1 | 88.7 | 11850 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.11 · 11/11 kV · 3×95 mm² | 11/11 kV | 95 | 13.3 | 7.6 | 48 | 9.6 | 93.8 | 13600 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.11 · 11/11 kV · 3×120 mm² | 11/11 kV | 120 | 15.3 | 7.6 | 53 | 9.9 | 98.7 | 15400 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.11 · 11/11 kV · 3×150 mm² | 11/11 kV | 150 | 17.2 | 7.6 | 56 | 10.3 | 103 | 17250 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.11 · 11/11 kV · 3×185 mm² | 11/11 kV | 185 | 18.8 | 7.6 | 56 | 10.7 | 108 | 19000 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 209.11 · 11/11 kV · 3×240 mm² | 11/11 kV | 240 | 21.7 | 7.6 | 77 | 11.3 | 116 | 22800 | Type 209 · Composite Screened · 1 Pilot · 1.1–11 kV
| Type 210.1 · 1.1/1.1 kV · 3×1.5 mm² | 1.1/1.1 kV | 1.5 | 1.6 | 1.4 | 6.2 | 3 | 25.6 | 1000 | Type 210 · Hand-Held Drill · 1 Pilot · 1.1/1.1 kV
| Type 210.1 · 1.1/1.1 kV · 3×2.5 mm² | 1.1/1.1 kV | 2.5 | 2.1 | 1.5 | 6.9 | 3 | 26.8 | 1100 | Type 210 · Hand-Held Drill · 1 Pilot · 1.1/1.1 kV
| Type 240.1 · 1.1/1.1 kV · 3×6 mm² | 1.1/1.1 kV | 6 | 3.5 | 1.5 | 8.2 | 3.8 | 31 | 1500 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 10 | 4.6 | 1.5 | 8.2 | 3.8 | 33.3 | 1750 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 | 6.2 | 1.6 | 10 | 4 | 37.3 | 2300 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 | 7.2 | 1.6 | 12 | 4.3 | 40.3 | 2950 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 | 8.4 | 1.6 | 14 | 4.6 | 43.6 | 3500 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 9.7 | 1.7 | 14 | 5 | 47.7 | 4250 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 12 | 1.8 | 16 | 5.4 | 54 | 5650 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 13.3 | 2 | 18 | 6 | 58.9 | 6700 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 15.3 | 2.1 | 21 | 6.4 | 64.6 | 8150 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 17.2 | 2.3 | 23 | 6.9 | 70.4 | 9900 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 | 18.8 | 2.5 | 30 | 7.4 | 76.5 | 11950 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 | 21.7 | 2.8 | 34 | 8.2 | 85.5 | 15050 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.1 · 1.1/1.1 kV · 3×300 mm² | 1.1/1.1 kV | 300 | 24.3 | 3 | 49 | 8.8 | 94.3 | 18700 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×16 mm² | 3.3/3.3 kV | 16 | 6.2 | 3 | 14 | 5.3 | 47.3 | 3400 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×25 mm² | 3.3/3.3 kV | 25 | 7.2 | 3 | 15 | 5.6 | 50.4 | 4100 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×35 mm² | 3.3/3.3 kV | 35 | 8.4 | 3 | 16 | 5.9 | 53.5 | 4750 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 | 9.7 | 3 | 17 | 6.3 | 57.2 | 5550 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 12 | 3 | 19 | 6.6 | 62.6 | 6900 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 13.3 | 3 | 21 | 7.1 | 66.4 | 7850 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 15.3 | 3 | 27 | 7.4 | 72 | 9550 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 17.2 | 3 | 32 | 7.8 | 76.7 | 11300 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 | 18.8 | 3 | 42 | 8.2 | 82.3 | 13300 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 | 21.7 | 3 | 48 | 8.8 | 89.6 | 16150 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.3 · 3.3/3.3 kV · 3×300 mm² | 3.3/3.3 kV | 300 | 24.3 | 3 | 63 | 9.4 | 97.7 | 19800 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×16 mm² | 6.6/6.6 kV | 16 | 6.2 | 5 | 17 | 6.4 | 58.2 | 4800 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×25 mm² | 6.6/6.6 kV | 25 | 7.2 | 5 | 19 | 6.7 | 61.7 | 5700 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×35 mm² | 6.6/6.6 kV | 35 | 8.4 | 5 | 21 | 7 | 64.8 | 6450 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×50 mm² | 6.6/6.6 kV | 50 | 9.7 | 5 | 22 | 7.3 | 68.2 | 7300 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 | 12 | 5 | 23 | 7.7 | 73.8 | 8800 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 | 13.3 | 5 | 30 | 8.1 | 78 | 10200 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 | 15.3 | 5 | 32 | 8.5 | 83.2 | 11800 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 | 17.2 | 5 | 46 | 8.9 | 89.2 | 14100 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 | 18.8 | 5 | 48 | 9.3 | 93.6 | 15850 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 | 21.7 | 5 | 53 | 9.9 | 101 | 18850 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.6 · 6.6/6.6 kV · 3×300 mm² | 6.6/6.6 kV | 300 | 24.3 | 5 | 71 | 10.4 | 109 | 22750 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.11 · 11/11 kV · 3×25 mm² | 11/11 kV | 25 | 7.2 | 7.6 | 24 | 8.1 | 75.9 | 8150 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.11 · 11/11 kV · 3×35 mm² | 11/11 kV | 35 | 8.4 | 7.6 | 30 | 8.4 | 79.6 | 9300 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.11 · 11/11 kV · 3×50 mm² | 11/11 kV | 50 | 9.7 | 7.6 | 32 | 8.7 | 83 | 10250 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.11 · 11/11 kV · 3×70 mm² | 11/11 kV | 70 | 12 | 7.6 | 35 | 9.1 | 88.7 | 12100 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.11 · 11/11 kV · 3×95 mm² | 11/11 kV | 95 | 13.3 | 7.6 | 48 | 9.6 | 93.8 | 13850 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.11 · 11/11 kV · 3×120 mm² | 11/11 kV | 120 | 15.3 | 7.6 | 53 | 9.9 | 98.7 | 15650 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.11 · 11/11 kV · 3×150 mm² | 11/11 kV | 150 | 17.2 | 7.6 | 56 | 10.3 | 103 | 17650 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.11 · 11/11 kV · 3×185 mm² | 11/11 kV | 185 | 18.8 | 7.6 | 56 | 10.7 | 108 | 19450 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 240.11 · 11/11 kV · 3×240 mm² | 11/11 kV | 240 | 21.7 | 7.6 | 77 | 11.3 | 116 | 23400 | Type 240 · Composite Screened · 3 Pilots · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×6 mm² | 1.1/1.1 kV | 6 | 3.5 | 1.5 | 1 | 3.8 | 29.9 | 1300 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 10 | 4.6 | 1.5 | 1.5 | 3.8 | 32 | 1550 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 | 6.2 | 1.6 | 3 | 3.9 | 35.9 | 2000 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 | 7.2 | 1.6 | 4.5 | 4.2 | 38.9 | 2550 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 | 8.4 | 1.6 | 6 | 4.4 | 42 | 3100 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 9.7 | 1.7 | 8 | 4.9 | 46.3 | 3800 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 12 | 1.8 | 12.5 | 5.3 | 52.4 | 5100 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 13.3 | 2 | 12.5 | 5.8 | 57.1 | 6050 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 15.3 | 2.1 | 13.75 | 6.3 | 62.9 | 7450 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 17.2 | 2.3 | 17 | 6.7 | 68.6 | 9100 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 | 18.8 | 2.5 | 22 | 7.3 | 74.4 | 10850 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 | 21.7 | 2.8 | 27 | 8 | 83.2 | 13700 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 · 1.1/1.1 kV · 3×300 mm² | 1.1/1.1 kV | 300 | 24.3 | 3 | 35.2 | 8.7 | 90.8 | 16700 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×16 mm² | 3.3/3.3 kV | 16 | 6.2 | 3 | 3 | 5 | 45 | 2850 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×25 mm² | 3.3/3.3 kV | 25 | 7.2 | 3 | 4.5 | 5.3 | 48.2 | 3500 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×35 mm² | 3.3/3.3 kV | 35 | 8.4 | 3 | 6 | 5.6 | 51.2 | 4100 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 | 9.7 | 3 | 8 | 6 | 55 | 4850 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 12 | 3 | 12.5 | 6.4 | 60.6 | 6200 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 13.3 | 3 | 16 | 6.8 | 64.2 | 7150 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 15.3 | 3 | 20 | 7.2 | 69.3 | 8550 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 17.2 | 3 | 27 | 7.6 | 74.2 | 10300 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 | 18.8 | 3 | 35.2 | 8 | 78.5 | 11900 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 | 21.7 | 3 | 39.5 | 8.6 | 85.8 | 14500 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.3 · 3.3/3.3 kV · 3×300 mm² | 3.3/3.3 kV | 300 | 24.3 | 3 | 50 | 9.1 | 92.3 | 17350 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×16 mm² | 6.6/6.6 kV | 16 | 6.2 | 5 | 3 | 6.1 | 55.9 | 4100 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×25 mm² | 6.6/6.6 kV | 25 | 7.2 | 5 | 4.5 | 6.4 | 59.4 | 4950 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×35 mm² | 6.6/6.6 kV | 35 | 8.4 | 5 | 6 | 6.7 | 62.5 | 5600 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×50 mm² | 6.6/6.6 kV | 50 | 9.7 | 5 | 8 | 7.1 | 66.2 | 6450 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 | 12 | 5 | 12.5 | 7.4 | 71.7 | 7900 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 | 13.3 | 5 | 16 | 7.9 | 75.5 | 9050 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 | 15.3 | 5 | 20 | 8.3 | 80.6 | 10650 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 | 17.2 | 5 | 27 | 8.6 | 85.1 | 12350 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 | 18.8 | 5 | 35.2 | 9 | 89.5 | 14100 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 | 21.7 | 5 | 39.5 | 9.6 | 96.8 | 16850 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.6 · 6.6/6.6 kV · 3×300 mm² | 6.6/6.6 kV | 300 | 24.3 | 5 | 50 | 10.2 | 104 | 19950 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.11 · 11/11 kV · 3×25 mm² | 11/11 kV | 25 | 7.2 | 7.6 | 4.5 | 7.8 | 73.8 | 7200 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.11 · 11/11 kV · 3×35 mm² | 11/11 kV | 35 | 8.4 | 7.6 | 6 | 8.1 | 76.8 | 8000 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.11 · 11/11 kV · 3×50 mm² | 11/11 kV | 50 | 9.7 | 7.6 | 8 | 8.5 | 80.5 | 8950 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.11 · 11/11 kV · 3×70 mm² | 11/11 kV | 70 | 12 | 7.6 | 12.5 | 8.9 | 86.1 | 10600 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.11 · 11/11 kV · 3×95 mm² | 11/11 kV | 95 | 13.3 | 7.6 | 16 | 9.3 | 89.7 | 11800 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.11 · 11/11 kV · 3×120 mm² | 11/11 kV | 120 | 15.3 | 7.6 | 20 | 9.7 | 94.8 | 13500 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.11 · 11/11 kV · 3×150 mm² | 11/11 kV | 150 | 17.2 | 7.6 | 27 | 10 | 99.3 | 15400 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.11 · 11/11 kV · 3×185 mm² | 11/11 kV | 185 | 18.8 | 7.6 | 32 | 10.4 | 104 | 17200 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.11 · 11/11 kV · 3×240 mm² | 11/11 kV | 240 | 21.7 | 7.6 | 39.5 | 11 | 111 | 20350 | Type 241 · Semiconductive Screened · 3 Earths + 1 Pilot · 1.1–11 kV
| Type 241.1 SF · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 12.1 | 1.8 | 12.5 | 5.3 | 52.7 | 5250 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.1 SF · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 13.6 | 2 | 12.5 | 5.8 | 57.6 | 6350 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.1 SF · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 15.6 | 2.1 | 13.75 | 6.3 | 63.6 | 7850 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.1 SF · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 17.5 | 2.3 | 17 | 6.7 | 69.2 | 9550 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.1 SF · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 | 19 | 2.5 | 22 | 7.3 | 74.8 | 11150 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.1 SF · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 | 21.9 | 2.8 | 27 | 8 | 83.7 | 14050 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.1 SF · 1.1/1.1 kV · 3×300 mm² | 1.1/1.1 kV | 300 | 24.4 | 3 | 35.7 | 8.7 | 91.2 | 17150 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.3 SF · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 12.1 | 3 | 12.5 | 6.4 | 60.9 | 6350 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.3 SF · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 13.6 | 3 | 16 | 6.8 | 64.8 | 7500 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.3 SF · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 15.6 | 3 | 20 | 7.2 | 70 | 9000 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.3 SF · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 17.5 | 3 | 27 | 7.6 | 74.8 | 10750 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.3 SF · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 | 19 | 3 | 35.2 | 8 | 78.9 | 12250 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.3 SF · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 | 21.9 | 3 | 39.5 | 8.6 | 86.2 | 14850 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.3 SF · 3.3/3.3 kV · 3×300 mm² | 3.3/3.3 kV | 300 | 24.4 | 3 | 50 | 9.1 | 92.7 | 17750 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.6 SF · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 | 12.1 | 5 | 12.5 | 7.4 | 72 | 8200 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.6 SF · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 | 13.6 | 5 | 16 | 7.9 | 76.1 | 9450 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.6 SF · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 | 15.6 | 5 | 20 | 8.3 | 81.3 | 11100 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.6 SF · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 | 17.5 | 5 | 27 | 8.6 | 85.8 | 12900 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.6 SF · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 | 19 | 5 | 35.2 | 9 | 89.9 | 14450 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.6 SF · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 | 21.9 | 5 | 39.5 | 9.6 | 97.2 | 17250 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.6 SF · 6.6/6.6 kV · 3×300 mm² | 6.6/6.6 kV | 300 | 24.4 | 5 | 50 | 10.2 | 104 | 20400 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.11 SF · 11/11 kV · 3×70 mm² | 11/11 kV | 70 | 12.1 | 7.6 | 12.5 | 8.9 | 86.4 | 10900 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.11 SF · 11/11 kV · 3×95 mm² | 11/11 kV | 95 | 13.6 | 7.6 | 16 | 9.3 | 90.3 | 12250 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.11 SF · 11/11 kV · 3×120 mm² | 11/11 kV | 120 | 15.6 | 7.6 | 20 | 9.7 | 95.5 | 14050 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.11 SF · 11/11 kV · 3×150 mm² | 11/11 kV | 150 | 17.5 | 7.6 | 27 | 10 | 100 | 16000 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.11 SF · 11/11 kV · 3×185 mm² | 11/11 kV | 185 | 19 | 7.6 | 35.2 | 10.4 | 104 | 17650 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 241.11 SF · 11/11 kV · 3×240 mm² | 11/11 kV | 240 | 21.9 | 7.6 | 39.5 | 11 | 111 | 20800 | Type 241SF · Max-Flexibility Semicon · 1.1–11 kV
| Type 245.1 UF · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 9.8 | 1.7 | 8 | 4.8 | 49.7 | 4250 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 245.1 UF · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 12 | 1.8 | 12.5 | 5.1 | 54.9 | 5550 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 245.1 UF · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 13.8 | 2 | 12.5 | 5.6 | 60.3 | 6750 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 245.1 UF · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 15.9 | 2.1 | 13.75 | 6 | 65.7 | 8450 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 245.1 UF · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 17.9 | 2.3 | 17 | 6.3 | 70.8 | 10100 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 245.3 UF · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 | 9.8 | 3 | 8 | 5.7 | 57.4 | 5250 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 245.3 UF · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 12 | 3 | 12.5 | 6 | 62.3 | 6600 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 245.3 UF · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 13.8 | 3 | 16 | 6.4 | 66.5 | 7800 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 245.3 UF · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 15.9 | 3 | 20 | 6.7 | 71.2 | 9500 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 245.3 UF · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 17.9 | 3 | 27 | 7 | 75.6 | 11200 | Type 245UF · Ultra-Flexible Shearer Chain · 1.1–3.3 kV
| Type 275.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 | 6 | 1.6 | 4.5 | 3.8 | 31.8 | 1700 | Type 275 · Shuttle Car Reeling · 1.1/1.1 kV
| Type 275.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 | 7.3 | 1.6 | 6.6 | 4 | 35 | 2250 | Type 275 · Shuttle Car Reeling · 1.1/1.1 kV
| Type 275.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 | 8.9 | 1.6 | 9 | 4.3 | 39 | 2850 | Type 275 · Shuttle Car Reeling · 1.1/1.1 kV
| Type 275.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 10.2 | 1.7 | 13.2 | 4.7 | 43.3 | 3700 | Type 275 · Shuttle Car Reeling · 1.1/1.1 kV
| Type 241.1 Superflex · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 |  | 1.8 | 13.8 |  | 53 | 4850 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.1 Superflex · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 |  | 2 | 10.7 |  | 58.8 | 5950 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.1 Superflex · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 |  | 2.1 | 13.8 |  | 62.5 | 7150 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.1 Superflex · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 |  | 2.3 | 17 |  | 67 | 8400 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.1 Superflex · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 |  | 2.5 | 20.7 |  | 75.1 | 10400 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.1 Superflex · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 |  | 2.8 | 27.1 |  | 85.7 | 13400 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.3 Superflex · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 |  | 3 | 13.8 |  | 61.2 | 5900 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.3 Superflex · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 |  | 3 | 17 |  | 65.9 | 7100 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.3 Superflex · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 |  | 3 | 20.7 |  | 68.9 | 8200 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.3 Superflex · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 |  | 3 | 27.1 |  | 72.5 | 9400 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.3 Superflex · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 |  | 3 | 31.7 |  | 79.4 | 11300 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.3 Superflex · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 |  | 3 | 40.7 |  | 88.3 | 14200 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.6 Superflex · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 |  | 5 | 13.8 |  | 72.1 | 7500 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.6 Superflex · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 |  | 5 | 17 |  | 77 | 8850 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.6 Superflex · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 |  | 5 | 20.7 |  | 79.9 | 10000 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.6 Superflex · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 |  | 5 | 27.1 |  | 83.3 | 11300 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.6 Superflex · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 |  | 5 | 31.7 |  | 90.2 | 13300 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 241.6 Superflex · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 |  | 5 | 40.7 |  | 99.1 | 16400 | Type 241 Superflex · Monorail Loop · 1.1–6.6 kV
| Type 245.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 |  | 2 | 3.4 | 4.1 | 42.6 | 2350 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 |  | 1.6 | 4.5 | 4.2 | 43.4 | 2690 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 |  | 1.6 | 6.9 | 4.4 | 45.6 | 3150 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 |  | 1.7 | 8.5 | 4.8 | 48.4 | 3900 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.1 · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 |  | 1.8 | 12.7 | 5.1 | 53.9 | 5010 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.1 · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 |  | 2 | 10.6 | 5.6 | 60.4 | 6300 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.1 · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 |  | 2.1 | 13.8 | 6 | 65.5 | 7650 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.1 · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 |  | 2.3 | 16.6 | 6.3 | 70.5 | 9150 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.3 · 3.3/3.3 kV · 3×25 mm² | 3.3/3.3 kV | 25 |  | 3 | 4.5 | 5.2 | 51.1 | 3380 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.3 · 3.3/3.3 kV · 3×35 mm² | 3.3/3.3 kV | 35 |  | 3 | 6.9 | 5.4 | 54.5 | 3980 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.3 · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 |  | 3 | 8.5 | 5.7 | 56.8 | 4900 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.3 · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 |  | 3 | 12.7 | 6 | 61.2 | 5920 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.3 · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 |  | 3 | 16.6 | 6.4 | 66.6 | 7390 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.3 · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 |  | 3 | 21.2 | 6.7 | 71 | 8700 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.3 · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 |  | 3 | 26.5 | 7 | 75.2 | 10280 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.6 · 6.6/6.6 kV · 3×50 mm² | 6.6/6.6 kV | 50 |  | 5 | 8.5 | 6.7 | 67.2 | 6350 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.6 · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 |  | 5 | 12.7 | 7 | 71.7 | 7550 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.6 · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 |  | 5 | 16.6 | 7.4 | 77.1 | 9050 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.6 · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 |  | 5 | 21.2 | 7.7 | 81.3 | 10500 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 245.6 · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 |  | 5 | 26.5 | 8 | 85.8 | 12100 | Type 245 · Longwall Shearer · 3 Earths + 3 Pilots · 1.1–6.6 kV
| Type 260.1 · 1.1/1.1 kV · 3×6 mm² | 1.1/1.1 kV | 6 |  | 1.5 | 7.2 | 3.8 | 36.9 | 2300 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 10 |  | 1.5 | 8.6 | 3.8 | 39.5 | 2650 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 |  | 1.6 | 9.6 | 4 | 46.5 | 4100 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 |  | 1.6 | 11.3 | 4.3 | 50.4 | 4950 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 |  | 1.6 | 12.4 | 4.6 | 53.8 | 5760 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 |  | 1.7 | 14.1 | 5 | 58.4 | 6790 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 |  | 1.8 | 16.5 | 5.4 | 64.6 | 8370 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 |  | 2 | 18.2 | 6 | 71.4 | 10030 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 |  | 2.1 | 20.3 | 6.4 | 77.2 | 11760 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 |  | 2.3 | 22.3 | 6.9 | 83 | 13720 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 |  | 2.5 | 30.2 | 7.4 | 90 | 16100 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 |  | 2.8 | 33.6 | 8.2 | 103 | 21500 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.1 · 1.1/1.1 kV · 3×300 mm² | 1.1/1.1 kV | 300 |  | 3 | 50.1 | 8.8 | 112.1 | 25900 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×16 mm² | 3.3/3.3 kV | 16 |  | 3 | 13.1 | 5.3 | 56.9 | 5660 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×25 mm² | 3.3/3.3 kV | 25 |  | 3 | 14.8 | 5.6 | 60.8 | 6610 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×35 mm² | 3.3/3.3 kV | 35 |  | 3 | 15.8 | 5.9 | 66.3 | 7790 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 |  | 3 | 17.2 | 6.3 | 70.4 | 8860 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 |  | 3 | 18.6 | 6.6 | 75.3 | 10440 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 |  | 3 | 20.3 | 7.1 | 78.9 | 11560 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 |  | 3 | 27.2 | 7.4 | 84.7 | 13500 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 |  | 3 | 39.6 | 7.8 | 95 | 17790 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 |  | 3 | 42.2 | 8.2 | 100.4 | 19900 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 |  | 3 | 46.6 | 8.8 | 107.3 | 23000 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.3 · 3.3/3.3 kV · 3×300 mm² | 3.3/3.3 kV | 300 |  | 3 | 63.2 | 9.4 | 115.4 | 27100 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×16 mm² | 6.6/6.6 kV | 16 |  | 5 | 17.2 | 6.4 | 70.1 | 7960 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×25 mm² | 6.6/6.6 kV | 25 |  | 5 | 18.6 | 6.7 | 74 | 8970 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×35 mm² | 6.6/6.6 kV | 35 |  | 5 | 18.6 | 7 | 77.4 | 9900 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×50 mm² | 6.6/6.6 kV | 50 |  | 5 | 21.3 | 7.3 | 81.2 | 11020 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 |  | 5 | 23.4 | 7.7 | 90.7 | 14560 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 |  | 5 | 29.2 | 8.1 | 94.8 | 16100 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 |  | 5 | 31.7 | 8.5 | 100.2 | 18070 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 |  | 5 | 45.7 | 8.9 | 106.2 | 20800 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 |  | 5 | 48.4 | 9.3 | 111.5 | 23000 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 |  | 5 | 52.8 | 9.9 | 118.4 | 26300 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.6 · 6.6/6.6 kV · 3×300 mm² | 6.6/6.6 kV | 300 |  | 5 | 71.5 | 10.4 | 126.3 | 30600 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.11 · 11/11 kV · 3×25 mm² | 11/11 kV | 25 |  | 7.6 | 23.7 | 8.1 | 92.7 | 13800 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.11 · 11/11 kV · 3×35 mm² | 11/11 kV | 35 |  | 7.6 | 30.2 | 8.4 | 96.7 | 15280 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.11 · 11/11 kV · 3×50 mm² | 11/11 kV | 50 |  | 7.6 | 31.7 | 8.7 | 100.6 | 16640 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.11 · 11/11 kV · 3×70 mm² | 11/11 kV | 70 |  | 7.6 | 34.1 | 9.1 | 105.8 | 18670 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.11 · 11/11 kV · 3×95 mm² | 11/11 kV | 95 |  | 7.6 | 47.5 | 9.6 | 110.7 | 20800 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.11 · 11/11 kV · 3×120 mm² | 11/11 kV | 120 |  | 7.6 | 51 | 9.9 | 115.8 | 22900 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.11 · 11/11 kV · 3×150 mm² | 11/11 kV | 150 |  | 7.6 | 53.7 | 10.3 | 120.5 | 25100 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
| Type 260.11 · 11/11 kV · 3×185 mm² | 11/11 kV | 185 |  | 7.6 | 57.2 | 10.7 | 125.9 | 27500 | Type 260 · Pliable SWA Armoured Feeder · 1.1–11 kV
For composite-screened types (209, 210, 240, 245, 260), 'Screen / earth (mm²)' gives the metallic copper cross-section of each phase screen; for semiconductive-screened/cradle types (241, 241SF, 241 Superflex, 245UF, 275), it gives the cross-section of each of the three interstitial earth conductors.
Masses have been converted from kg/100 m to kg/km (× 10) for consistency across all PDP tables.

## Electrical parameters
AS/NZS 1802 Underground Coal Mining Reeling & Trailing Cables – Electrical parameters (174) (174)
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1802-underground-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1802. Values for your order are confirmed in the quotation.
Type · grade · size | Voltage U0/U | Phase area (mm²) | AC resistance 90 °C (Ω/km) | Reactance 50 Hz (Ω/km) | Voltage drop (mV/A·m) | Capacitance (µF/km) | Series
Type 209.1 · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 10 | 2.58 | 0.13 | 4.47 | 0.314 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 | 1.58 | 0.118 | 2.74 | 0.379 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 | 0.951 | 0.112 | 1.66 | 0.432 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 | 0.698 | 0.107 | 1.22 | 0.493 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 0.523 | 0.104 | 0.924 | 0.526 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 0.346 | 0.0981 | 0.623 | 0.599 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 0.271 | 0.0955 | 0.498 | 0.591 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 0.21 | 0.0925 | 0.397 | 0.64 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 0.166 | 0.0907 | 0.328 | 0.652 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 | 0.137 | 0.0902 | 0.284 | 0.657 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 | 0.107 | 0.0883 | 0.24 | 0.672 | Type 209 · 1.1–11 kV
Type 209.1 · 1.1/1.1 kV · 3×300 mm² | 1.1/1.1 kV | 300 | 0.085 | 0.0873 | 0.211 | 0.719 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×16 mm² | 3.3/3.3 kV | 16 | 1.58 | 0.131 | 2.75 | 0.255 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×25 mm² | 3.3/3.3 kV | 25 | 0.951 | 0.125 | 1.66 | 0.28 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×35 mm² | 3.3/3.3 kV | 35 | 0.698 | 0.119 | 1.23 | 0.311 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 | 0.523 | 0.114 | 0.927 | 0.347 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 0.346 | 0.106 | 0.627 | 0.408 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 0.271 | 0.102 | 0.502 | 0.439 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 0.21 | 0.0985 | 0.402 | 0.492 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 0.166 | 0.0954 | 0.332 | 0.541 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 | 0.137 | 0.0942 | 0.288 | 0.584 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 | 0.106 | 0.0906 | 0.242 | 0.659 | Type 209 · 1.1–11 kV
Type 209.3 · 3.3/3.3 kV · 3×300 mm² | 3.3/3.3 kV | 300 | 0.0849 | 0.089 | 0.213 | 0.727 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×16 mm² | 6.6/6.6 kV | 16 | 1.58 | 0.143 | 2.75 | 0.181 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×25 mm² | 6.6/6.6 kV | 25 | 0.951 | 0.137 | 1.66 | 0.193 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×35 mm² | 6.6/6.6 kV | 35 | 0.698 | 0.13 | 1.23 | 0.212 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×50 mm² | 6.6/6.6 kV | 50 | 0.523 | 0.124 | 0.931 | 0.234 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 | 0.346 | 0.116 | 0.632 | 0.271 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 | 0.271 | 0.113 | 0.509 | 0.292 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 | 0.21 | 0.108 | 0.409 | 0.325 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 | 0.166 | 0.105 | 0.34 | 0.354 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 | 0.136 | 0.102 | 0.294 | 0.381 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 | 0.106 | 0.0981 | 0.25 | 0.426 | Type 209 · 1.1–11 kV
Type 209.6 · 6.6/6.6 kV · 3×300 mm² | 6.6/6.6 kV | 300 | 0.0845 | 0.0959 | 0.221 | 0.467 | Type 209 · 1.1–11 kV
Type 209.11 · 11/11 kV · 3×25 mm² | 11/11 kV | 25 | 0.951 | 0.15 | 1.67 | 0.15 | Type 209 · 1.1–11 kV
Type 209.11 · 11/11 kV · 3×35 mm² | 11/11 kV | 35 | 0.698 | 0.143 | 1.23 | 0.163 | Type 209 · 1.1–11 kV
Type 209.11 · 11/11 kV · 3×50 mm² | 11/11 kV | 50 | 0.523 | 0.136 | 0.936 | 0.178 | Type 209 · 1.1–11 kV
Type 209.11 · 11/11 kV · 3×70 mm² | 11/11 kV | 70 | 0.346 | 0.127 | 0.638 | 0.204 | Type 209 · 1.1–11 kV
Type 209.11 · 11/11 kV · 3×95 mm² | 11/11 kV | 95 | 0.271 | 0.124 | 0.516 | 0.219 | Type 209 · 1.1–11 kV
Type 209.11 · 11/11 kV · 3×120 mm² | 11/11 kV | 120 | 0.21 | 0.119 | 0.418 | 0.241 | Type 209 · 1.1–11 kV
Type 209.11 · 11/11 kV · 3×150 mm² | 11/11 kV | 150 | 0.165 | 0.114 | 0.347 | 0.261 | Type 209 · 1.1–11 kV
Type 209.11 · 11/11 kV · 3×185 mm² | 11/11 kV | 185 | 0.136 | 0.111 | 0.304 | 0.279 | Type 209 · 1.1–11 kV
Type 209.11 · 11/11 kV · 3×240 mm² | 11/11 kV | 240 | 0.106 | 0.107 | 0.261 | 0.309 | Type 209 · 1.1–11 kV
Type 210.1 · 1.1/1.1 kV · 3×1.5 mm² | 1.1/1.1 kV | 1.5 | 17.5 | 0.187 | 30.3 | 0.165 | Type 210 · 1.1/1.1 kV
Type 210.1 · 1.1/1.1 kV · 3×2.5 mm² | 1.1/1.1 kV | 2.5 | 10.5 | 0.174 | 18.2 | 0.184 | Type 210 · 1.1/1.1 kV
Type 240.1 · 1.1/1.1 kV · 3×6 mm² | 1.1/1.1 kV | 6 | 4.32 | 0.141 | 7.49 | 0.259 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 10 | 2.58 | 0.13 | 4.47 | 0.314 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 | 1.58 | 0.118 | 2.74 | 0.379 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 | 0.951 | 0.112 | 1.66 | 0.432 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 | 0.698 | 0.107 | 1.22 | 0.493 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 0.523 | 0.104 | 0.924 | 0.526 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 0.346 | 0.0981 | 0.623 | 0.599 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 0.271 | 0.0955 | 0.498 | 0.591 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 0.21 | 0.0925 | 0.397 | 0.64 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 0.166 | 0.0907 | 0.328 | 0.652 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 | 0.137 | 0.0902 | 0.284 | 0.657 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 | 0.107 | 0.0883 | 0.24 | 0.672 | Type 240 · 1.1–11 kV
Type 240.1 · 1.1/1.1 kV · 3×300 mm² | 1.1/1.1 kV | 300 | 0.085 | 0.0873 | 0.211 | 0.719 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×16 mm² | 3.3/3.3 kV | 16 | 1.58 | 0.131 | 2.75 | 0.255 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×25 mm² | 3.3/3.3 kV | 25 | 0.951 | 0.125 | 1.66 | 0.28 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×35 mm² | 3.3/3.3 kV | 35 | 0.698 | 0.119 | 1.23 | 0.311 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 | 0.523 | 0.114 | 0.927 | 0.347 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 0.346 | 0.106 | 0.627 | 0.408 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 0.271 | 0.102 | 0.502 | 0.439 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 0.21 | 0.0985 | 0.402 | 0.492 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 0.166 | 0.0954 | 0.332 | 0.541 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 | 0.137 | 0.0942 | 0.288 | 0.584 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 | 0.106 | 0.0906 | 0.242 | 0.659 | Type 240 · 1.1–11 kV
Type 240.3 · 3.3/3.3 kV · 3×300 mm² | 3.3/3.3 kV | 300 | 0.0849 | 0.089 | 0.213 | 0.727 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×16 mm² | 6.6/6.6 kV | 16 | 1.58 | 0.143 | 2.75 | 0.181 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×25 mm² | 6.6/6.6 kV | 25 | 0.951 | 0.137 | 1.66 | 0.193 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×35 mm² | 6.6/6.6 kV | 35 | 0.698 | 0.13 | 1.23 | 0.212 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×50 mm² | 6.6/6.6 kV | 50 | 0.523 | 0.124 | 0.931 | 0.234 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 | 0.346 | 0.116 | 0.632 | 0.271 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 | 0.271 | 0.113 | 0.509 | 0.292 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 | 0.21 | 0.108 | 0.409 | 0.325 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 | 0.166 | 0.105 | 0.34 | 0.354 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 | 0.136 | 0.102 | 0.294 | 0.381 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 | 0.106 | 0.0981 | 0.25 | 0.426 | Type 240 · 1.1–11 kV
Type 240.6 · 6.6/6.6 kV · 3×300 mm² | 6.6/6.6 kV | 300 | 0.0845 | 0.0959 | 0.221 | 0.467 | Type 240 · 1.1–11 kV
Type 240.11 · 11/11 kV · 3×25 mm² | 11/11 kV | 25 | 0.951 | 0.15 | 1.67 | 0.15 | Type 240 · 1.1–11 kV
Type 240.11 · 11/11 kV · 3×35 mm² | 11/11 kV | 35 | 0.698 | 0.143 | 1.23 | 0.163 | Type 240 · 1.1–11 kV
Type 240.11 · 11/11 kV · 3×50 mm² | 11/11 kV | 50 | 0.523 | 0.136 | 0.936 | 0.178 | Type 240 · 1.1–11 kV
Type 240.11 · 11/11 kV · 3×70 mm² | 11/11 kV | 70 | 0.346 | 0.127 | 0.638 | 0.204 | Type 240 · 1.1–11 kV
Type 240.11 · 11/11 kV · 3×95 mm² | 11/11 kV | 95 | 0.271 | 0.124 | 0.516 | 0.219 | Type 240 · 1.1–11 kV
Type 240.11 · 11/11 kV · 3×120 mm² | 11/11 kV | 120 | 0.21 | 0.119 | 0.418 | 0.241 | Type 240 · 1.1–11 kV
Type 240.11 · 11/11 kV · 3×150 mm² | 11/11 kV | 150 | 0.165 | 0.114 | 0.347 | 0.261 | Type 240 · 1.1–11 kV
Type 240.11 · 11/11 kV · 3×185 mm² | 11/11 kV | 185 | 0.136 | 0.111 | 0.304 | 0.279 | Type 240 · 1.1–11 kV
Type 240.11 · 11/11 kV · 3×240 mm² | 11/11 kV | 240 | 0.106 | 0.107 | 0.261 | 0.309 | Type 240 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×6 mm² | 1.1/1.1 kV | 6 | 4.32 | 0.139 | 7.49 | 0.259 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 10 | 2.58 | 0.127 | 4.47 | 0.314 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 | 1.58 | 0.116 | 2.74 | 0.379 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 | 0.951 | 0.11 | 1.66 | 0.432 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 | 0.698 | 0.106 | 1.22 | 0.493 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 0.523 | 0.102 | 0.923 | 0.526 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 0.346 | 0.0965 | 0.622 | 0.599 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 0.271 | 0.0942 | 0.497 | 0.591 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 0.21 | 0.0912 | 0.397 | 0.64 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 0.166 | 0.0896 | 0.327 | 0.652 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 | 0.137 | 0.0885 | 0.283 | 0.657 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 | 0.107 | 0.0868 | 0.239 | 0.672 | Type 241 · 1.1–11 kV
Type 241.1 · 1.1/1.1 kV · 3×300 mm² | 1.1/1.1 kV | 300 | 0.0851 | 0.0848 | 0.208 | 0.719 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×16 mm² | 3.3/3.3 kV | 16 | 1.58 | 0.129 | 2.75 | 0.255 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×25 mm² | 3.3/3.3 kV | 25 | 0.951 | 0.123 | 1.66 | 0.28 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×35 mm² | 3.3/3.3 kV | 35 | 0.698 | 0.117 | 1.23 | 0.311 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 | 0.523 | 0.112 | 0.926 | 0.347 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 0.346 | 0.105 | 0.626 | 0.408 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 0.271 | 0.101 | 0.501 | 0.439 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 0.21 | 0.0965 | 0.4 | 0.492 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 0.166 | 0.0934 | 0.33 | 0.541 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 | 0.137 | 0.0911 | 0.285 | 0.584 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 | 0.107 | 0.0878 | 0.24 | 0.659 | Type 241 · 1.1–11 kV
Type 241.3 · 3.3/3.3 kV · 3×300 mm² | 3.3/3.3 kV | 300 | 0.0851 | 0.0854 | 0.209 | 0.727 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×16 mm² | 6.6/6.6 kV | 16 | 1.58 | 0.141 | 2.75 | 0.181 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×25 mm² | 6.6/6.6 kV | 25 | 0.951 | 0.135 | 1.66 | 0.193 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×35 mm² | 6.6/6.6 kV | 35 | 0.698 | 0.129 | 1.23 | 0.212 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×50 mm² | 6.6/6.6 kV | 50 | 0.523 | 0.123 | 0.931 | 0.234 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 | 0.346 | 0.115 | 0.632 | 0.271 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 | 0.271 | 0.111 | 0.507 | 0.292 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 | 0.21 | 0.106 | 0.407 | 0.325 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 | 0.166 | 0.102 | 0.337 | 0.354 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 | 0.137 | 0.0997 | 0.293 | 0.381 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 | 0.106 | 0.0957 | 0.247 | 0.426 | Type 241 · 1.1–11 kV
Type 241.6 · 6.6/6.6 kV · 3×300 mm² | 6.6/6.6 kV | 300 | 0.0847 | 0.0927 | 0.217 | 0.467 | Type 241 · 1.1–11 kV
Type 241.11 · 11/11 kV · 3×25 mm² | 11/11 kV | 25 | 0.951 | 0.148 | 1.67 | 0.15 | Type 241 · 1.1–11 kV
Type 241.11 · 11/11 kV · 3×35 mm² | 11/11 kV | 35 | 0.698 | 0.141 | 1.23 | 0.163 | Type 241 · 1.1–11 kV
Type 241.11 · 11/11 kV · 3×50 mm² | 11/11 kV | 50 | 0.523 | 0.135 | 0.936 | 0.178 | Type 241 · 1.1–11 kV
Type 241.11 · 11/11 kV · 3×70 mm² | 11/11 kV | 70 | 0.346 | 0.126 | 0.638 | 0.204 | Type 241 · 1.1–11 kV
Type 241.11 · 11/11 kV · 3×95 mm² | 11/11 kV | 95 | 0.271 | 0.122 | 0.515 | 0.219 | Type 241 · 1.1–11 kV
Type 241.11 · 11/11 kV · 3×120 mm² | 11/11 kV | 120 | 0.21 | 0.116 | 0.416 | 0.241 | Type 241 · 1.1–11 kV
Type 241.11 · 11/11 kV · 3×150 mm² | 11/11 kV | 150 | 0.165 | 0.112 | 0.345 | 0.261 | Type 241 · 1.1–11 kV
Type 241.11 · 11/11 kV · 3×185 mm² | 11/11 kV | 185 | 0.136 | 0.109 | 0.302 | 0.279 | Type 241 · 1.1–11 kV
Type 241.11 · 11/11 kV · 3×240 mm² | 11/11 kV | 240 | 0.106 | 0.104 | 0.257 | 0.309 | Type 241 · 1.1–11 kV
Type 241.1 SF · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 0.346 | 0.0985 | 0.623 | 0.619 | Type 241SF · 1.1–11 kV
Type 241.1 SF · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 0.271 | 0.0968 | 0.498 | 0.622 | Type 241SF · 1.1–11 kV
Type 241.1 SF · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 0.21 | 0.0938 | 0.398 | 0.673 | Type 241SF · 1.1–11 kV
Type 241.1 SF · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 0.166 | 0.0922 | 0.329 | 0.685 | Type 241SF · 1.1–11 kV
Type 241.1 SF · 1.1/1.1 kV · 3×185 mm² | 1.1/1.1 kV | 185 | 0.137 | 0.0898 | 0.284 | 0.674 | Type 241SF · 1.1–11 kV
Type 241.1 SF · 1.1/1.1 kV · 3×240 mm² | 1.1/1.1 kV | 240 | 0.107 | 0.0881 | 0.24 | 0.689 | Type 241SF · 1.1–11 kV
Type 241.1 SF · 1.1/1.1 kV · 3×300 mm² | 1.1/1.1 kV | 300 | 0.0851 | 0.0862 | 0.21 | 0.736 | Type 241SF · 1.1–11 kV
Type 241.3 SF · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 0.346 | 0.107 | 0.627 | 0.422 | Type 241SF · 1.1–11 kV
Type 241.3 SF · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 0.271 | 0.103 | 0.502 | 0.461 | Type 241SF · 1.1–11 kV
Type 241.3 SF · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 0.21 | 0.0991 | 0.402 | 0.517 | Type 241SF · 1.1–11 kV
Type 241.3 SF · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 0.166 | 0.0961 | 0.332 | 0.568 | Type 241SF · 1.1–11 kV
Type 241.3 SF · 3.3/3.3 kV · 3×185 mm² | 3.3/3.3 kV | 185 | 0.137 | 0.0924 | 0.286 | 0.6 | Type 241SF · 1.1–11 kV
Type 241.3 SF · 3.3/3.3 kV · 3×240 mm² | 3.3/3.3 kV | 240 | 0.107 | 0.0891 | 0.241 | 0.675 | Type 241SF · 1.1–11 kV
Type 241.3 SF · 3.3/3.3 kV · 3×300 mm² | 3.3/3.3 kV | 300 | 0.0851 | 0.0867 | 0.21 | 0.744 | Type 241SF · 1.1–11 kV
Type 241.6 SF · 6.6/6.6 kV · 3×70 mm² | 6.6/6.6 kV | 70 | 0.346 | 0.118 | 0.633 | 0.283 | Type 241SF · 1.1–11 kV
Type 241.6 SF · 6.6/6.6 kV · 3×95 mm² | 6.6/6.6 kV | 95 | 0.271 | 0.114 | 0.509 | 0.307 | Type 241SF · 1.1–11 kV
Type 241.6 SF · 6.6/6.6 kV · 3×120 mm² | 6.6/6.6 kV | 120 | 0.21 | 0.109 | 0.41 | 0.341 | Type 241SF · 1.1–11 kV
Type 241.6 SF · 6.6/6.6 kV · 3×150 mm² | 6.6/6.6 kV | 150 | 0.166 | 0.105 | 0.34 | 0.371 | Type 241SF · 1.1–11 kV
Type 241.6 SF · 6.6/6.6 kV · 3×185 mm² | 6.6/6.6 kV | 185 | 0.137 | 0.101 | 0.295 | 0.39 | Type 241SF · 1.1–11 kV
Type 241.6 SF · 6.6/6.6 kV · 3×240 mm² | 6.6/6.6 kV | 240 | 0.106 | 0.0971 | 0.249 | 0.436 | Type 241SF · 1.1–11 kV
Type 241.6 SF · 6.6/6.6 kV · 3×300 mm² | 6.6/6.6 kV | 300 | 0.0847 | 0.0941 | 0.219 | 0.478 | Type 241SF · 1.1–11 kV
Type 241.11 SF · 11/11 kV · 3×70 mm² | 11/11 kV | 70 | 0.346 | 0.129 | 0.64 | 0.212 | Type 241SF · 1.1–11 kV
Type 241.11 SF · 11/11 kV · 3×95 mm² | 11/11 kV | 95 | 0.271 | 0.125 | 0.517 | 0.229 | Type 241SF · 1.1–11 kV
Type 241.11 SF · 11/11 kV · 3×120 mm² | 11/11 kV | 120 | 0.21 | 0.119 | 0.418 | 0.252 | Type 241SF · 1.1–11 kV
Type 241.11 SF · 11/11 kV · 3×150 mm² | 11/11 kV | 150 | 0.165 | 0.115 | 0.348 | 0.273 | Type 241SF · 1.1–11 kV
Type 241.11 SF · 11/11 kV · 3×185 mm² | 11/11 kV | 185 | 0.136 | 0.11 | 0.303 | 0.286 | Type 241SF · 1.1–11 kV
Type 241.11 SF · 11/11 kV · 3×240 mm² | 11/11 kV | 240 | 0.106 | 0.106 | 0.26 | 0.317 | Type 241SF · 1.1–11 kV
Type 245.1 UF · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 0.523 | 0.114 | 0.927 | 0.544 | Type 245UF · 1.1–3.3 kV
Type 245.1 UF · 1.1/1.1 kV · 3×70 mm² | 1.1/1.1 kV | 70 | 0.346 | 0.107 | 0.627 | 0.614 | Type 245UF · 1.1–3.3 kV
Type 245.1 UF · 1.1/1.1 kV · 3×95 mm² | 1.1/1.1 kV | 95 | 0.271 | 0.103 | 0.502 | 0.63 | Type 245UF · 1.1–3.3 kV
Type 245.1 UF · 1.1/1.1 kV · 3×120 mm² | 1.1/1.1 kV | 120 | 0.21 | 0.0988 | 0.402 | 0.684 | Type 245UF · 1.1–3.3 kV
Type 245.1 UF · 1.1/1.1 kV · 3×150 mm² | 1.1/1.1 kV | 150 | 0.166 | 0.0956 | 0.332 | 0.698 | Type 245UF · 1.1–3.3 kV
Type 245.3 UF · 3.3/3.3 kV · 3×50 mm² | 3.3/3.3 kV | 50 | 0.523 | 0.121 | 0.93 | 0.359 | Type 245UF · 1.1–3.3 kV
Type 245.3 UF · 3.3/3.3 kV · 3×70 mm² | 3.3/3.3 kV | 70 | 0.346 | 0.113 | 0.63 | 0.418 | Type 245UF · 1.1–3.3 kV
Type 245.3 UF · 3.3/3.3 kV · 3×95 mm² | 3.3/3.3 kV | 95 | 0.271 | 0.108 | 0.505 | 0.467 | Type 245UF · 1.1–3.3 kV
Type 245.3 UF · 3.3/3.3 kV · 3×120 mm² | 3.3/3.3 kV | 120 | 0.21 | 0.103 | 0.405 | 0.525 | Type 245UF · 1.1–3.3 kV
Type 245.3 UF · 3.3/3.3 kV · 3×150 mm² | 3.3/3.3 kV | 150 | 0.166 | 0.0986 | 0.334 | 0.578 | Type 245UF · 1.1–3.3 kV
Type 275.1 · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 16 | 1.58 | 0.109 | 2.74 | 0.377 | Type 275 · 1.1/1.1 kV
Type 275.1 · 1.1/1.1 kV · 3×25 mm² | 1.1/1.1 kV | 25 | 0.951 | 0.102 | 1.66 | 0.443 | Type 275 · 1.1/1.1 kV
Type 275.1 · 1.1/1.1 kV · 3×35 mm² | 1.1/1.1 kV | 35 | 0.698 | 0.0963 | 1.22 | 0.521 | Type 275 · 1.1/1.1 kV
Type 275.1 · 1.1/1.1 kV · 3×50 mm² | 1.1/1.1 kV | 50 | 0.523 | 0.0943 | 0.92 | 0.551 | Type 275 · 1.1/1.1 kV
Electrical parameters are stated at 50 Hz and 90 °C maximum conductor operating temperature.
Three-phase voltage drop values (mV/A·m) are based on lagging power factor 0.8.

## Technical data
AS/NZS 1802 Underground Coal Mining Reeling & Trailing Cables – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1802-underground-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1802. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.1–11 kV (1.1/1.1, 3.3/3.3, 6.6/6.6 & 11/11 kV)
Key data | Conductor size | 1.5–300 mm² (3 phase cores, tinned copper)
Key data | Conductor temp. | +90 °C (Max. continuous · +250 °C short-circuit)
Key data | Min. temp. | −25 °C (Minimum installation temperature)
Key data | Min. bend radius | 6 × D / 10 × D (Fixed 6 × D · Dynamic reeling 10 × D)
Key data | Cable types | 10 types (255 sizes across Types 209 to 275)
Electrical | Rated voltage U0/U | 1.1/1.1, 3.3/3.3, 6.6/6.6 & 11/11 kV
Electrical | Earth-screen architecture | Composite Cu/PET (209–240, 260) or semicon (241–245, 275)
Electrical | Pilot conductor arrangement | 1 central pilot (209, 210, 241, 275) or 3 pilots (240, 245)
Electrical | Pilot max. DC resistance | ≤ 3.0 Ω/100 m (Type 245UF); ≤ 5.5 Ω/100 m (Type 210)
Thermal | Max. continuous conductor temp. | +90 °C
Thermal | Short-circuit temperature | +250 °C (5 s maximum)
Thermal | Min. installation temperature | −25 °C
Mechanical | Conductor stranding | Flexible stranded tinned annealed copper (AS/NZS 1125)
Mechanical | Minimum bend radius | 6 × D fixed; 10 × D dynamic flexing & reeling
Mechanical | Sheath reinforcement & armour | Open-weave textile braid (241/245/275); SWA pliable armour (260)
Resistance | Flame propagation | AS/NZS 1660.5.6 Category C1 flame retardant
Resistance | Oil & water immersion | HD-85-PCP heavy-duty oil, water & abrasion resistant
Resistance | Anti-corkscrewing design | Semiconductive cradle + open-weave reinforcement (Type 275)
Standards | Primary cable standard | AS/NZS 1802 (underground coal mining cables)
Standards | Compounds & conductors | AS/NZS 3808 (R-EP-90, HD-85-PCP); AS/NZS 1125
Identification | Phase core identification | Red, white, blue braid tracers (209/240) or printed numbers (241)
Identification | Outer sheath compound | Black heavy-duty HD-85-PCP polychloroprene (CPE/CSP optional)

## Construction
AS/NZS 1802 Underground Coal Mining Reeling & Trailing Cables – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1802-underground-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1802. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible tinned copper phase conductor | Flexible stranded tinned annealed copper per AS/NZS 1125 (extra-fine stranding on SF, Superflex and UF types) | AS/NZS 1125
2 | Conductor screen | Extruded semiconductive elastomer screen on 3.3/3.3 kV and above; polyester separator tape at 1.1/1.1 kV | AS/NZS 1802
3 | R-EP-90 EPR insulation | Thermoset ethylene propylene rubber (R-EP-90 per AS/NZS 3808) rated +90 °C continuous and +250 °C short-circuit | AS/NZS 3808
4 | Core earth screen (composite Cu/PET or semiconductive) | Composite tinned copper wire / polyester yarn braid (Types 209, 210, 240, 260) or semiconductive elastomer screen + 3 interstitial earths (Types 241, 245) | AS/NZS 1802
5 | Extensible pilot & interstitial earth cores | Central extensible EPR-insulated pilot (or 3 pilots on Types 240/245/245UF) plus 3 semiconductive-covered earth cores in interstices | AS/NZS 1802
6 | Open-weave anti-torsion reinforcement (or SWA on Type 260) | Open-weave textile reinforcement locked into the sheath (Types 241, 245, 275) or pliable galvanised steel wire strand armour (Type 260) | AS/NZS 1802
7 | Heavy-duty HD-85-PCP outer sheath | Flame-retardant (Category C1), oil-, water- and abrasion-resistant heavy-duty polychloroprene (HD-85-PCP per AS/NZS 3808) | AS/NZS 3808
| Composite Copper/Polyester Screened (Types 209, 210, 240, 260) | Individual tinned-copper/polyester composite earth screens over each phase core; 1 central pilot (209, 210, 260) or 3 interstitial pilots (240).
| Semiconductive Screened + 3 Interstitial Earths (Types 241, 241SF, 245, 245UF) | Replaces metallic core braids with semiconductive elastomer screens and 3 interstitial earth conductors for superior flexing in monorails and shearer chains.
| Shuttle Car Anti-Corkscrewing Reeling (Type 275) | Unscreened 1.1 kV phase cores locked in a semiconductive elastomer cradle with 3 interstitial earths, central pilot and open-weave reinforcement.

## Series
AS/NZS 1802 Underground Coal Mining Reeling & Trailing Cables – Series
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1802-underground-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1802. Values for your order are confirmed in the quotation.
Code | Series | Rating | Standard / class | Sizes | Typical use
209 | Type 209 | 1.1–11 kV | Composite screen | 43 | General underground trailing, continuous miners & pump feeders
210 | Type 210 | 1.1/1.1 kV | Composite screen | 2 | Hand-held boring machines, roof bolters & light portable drills
240 | Type 240 | 1.1–11 kV | Composite screen | 44 | Long feeder runs between transformer & gate-end box, continuous miners
241 | Type 241 | 1.1–11 kV | Semicon screen | 44 | Continuous miners, monorail DCB feeders & longwall peripherals
241SF | Type 241SF | 1.1–11 kV | Max. flexibility | 27 | Tight underground turns, continuous miners & monorail loops
241 Sup | Type 241 Superflex | 1.1–6.6 kV | Superflex | 18 | Compact monorail loops supplying DCBs and longwall faces
245 | Type 245 | 1.1–6.6 kV | Shearer cable | 20 | Longwall shearers, continuous miners & multi-pilot control loops
245UF | Type 245UF | 1.1–3.3 kV | Ultra-flexible | 10 | Tight-radius longwall shearer cable chains (bretby handlers)
260 | Type 260 | 1.1–11 kV | Pliable armoured | 43 | Armoured underground feeder runs to transportable substations
275 | Type 275 | 1.1/1.1 kV | Shuttle car reeling | 4 | High-speed reeling on underground coal shuttle cars (16–50 mm²)

## Quality and supply
AS/NZS 1802 Underground Coal Mining Reeling & Trailing Cables – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1802-underground-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1802. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor & pilot DC resistance and earth-screen continuity — 100 % drum verification of phase, earth and extensible pilot resistance per AS/NZS 1125 and AS/NZS 1802 | Every production length
Routine test | High-voltage AC dielectric & partial discharge test — 5-minute AC voltage withstand on all grades; partial discharge extinction test on 3.3/3.3 kV to 11/11 kV screened cores per AS/NZS 1802 | Every production length
Type test | Flame propagation (AS/NZS 1660.5.6 Category C1) — Self-extinguishing vertical flame test compliance to Category C1 as mandated for underground coal mines | Type approval & periodic audit
Type test | HD-85-PCP oil, water immersion & tear resistance — Tensile, elongation and tear retention after hot oil and water immersion per AS/NZS 3808 | Type approval & batch sample
Standard / approval | AS/NZS 1802 Underground Coal Mining Reeling & Trailing Cable
Standard / approval | AS/NZS 1660.5.6 Category C1 Flame Retardant
Standard / approval | NSW Resources Regulator / Dolomite & Underground Coal MDG 3608 Compliance
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX — AS/NZS 1802 — TYPE <CODE> — <U0/U kV> — 3 × <AREA> mm² — R-EP-90 / HD-85-PCP — C1 FLAME RETARDANT — YEAR — METRE MARK
Supply | Standard packing: 250 m, 500 m or custom face-length steel/timber mining drums
Supply | Outer sheath options: Black HD-85-PCP standard; high-visibility stripes or CPE/CSP on request
Supply | Export tariff code: HS 8544.60 (> 1,000 V underground mining cables)