## Request a quote
Request a quotation for AS/NZS 1972
Specify Type 1 (V-90/5V-90 PVC for ducted wiring), Type 2S (1.1/1.1 kV R-EP-90/HD-90-CPE) or Type 2S.3 (3.3/3.3 kV), individual vs collective screening, core count × mm² and any required pilot cores.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/as-nzs-1972-mine-feeder-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
AS/NZS 1972 Underground Mining Machine & Feeder Cables – Dimensions & mass (43) (43)
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1972-mine-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1972. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Type · grade · size | Voltage U0/U | Main cores | Core area (mm²) | Pilot cores | Conductor Ø (mm) | Insulation wall (mm) | Outer wall (mm) | Nominal OD (mm) | Total mass (kg/km) | Series
| Type 1 Ind. · 1.1/1.1 kV · 2×1.5 mm² | 1.1/1.1 kV | 2 | 1.5 | None | 1.6 | 0.8 | 0.8 | 10.2 | 150 | Type 1 · Individually Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Ind. · 1.1/1.1 kV · 3×1.5 mm² | 1.1/1.1 kV | 3 | 1.5 | None | 1.6 | 0.8 | 0.8 | 10.8 | 200 | Type 1 · Individually Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Ind. · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 3 | 10 | None | 4.6 | 1 | 1 | 18.1 | 600 | Type 1 · Individually Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Ind. · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 3 | 16 | None | 6.2 | 1 | 1.3 | 22 | 850 | Type 1 · Individually Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Ind. · 1.1/1.1 kV · 4×1.5 mm² | 1.1/1.1 kV | 4 | 1.5 | None | 1.6 | 0.8 | 0.8 | 11.9 | 250 | Type 1 · Individually Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Ind. · 1.1/1.1 kV · 4×10 mm² | 1.1/1.1 kV | 4 | 10 | None | 4.6 | 1 | 1.3 | 20.5 | 750 | Type 1 · Individually Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Ind. · 1.1/1.1 kV · 4×16 mm² | 1.1/1.1 kV | 4 | 16 | None | 6.2 | 1 | 1.3 | 24.3 | 1100 | Type 1 · Individually Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Coll. · 1.1/1.1 kV · 2×1.5 mm² | 1.1/1.1 kV | 2 | 1.5 | None | 1.6 | 0.8 | 0.8 | 9.4 | 150 | Type 1 · Collectively Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Coll. · 1.1/1.1 kV · 3×1.5 mm² | 1.1/1.1 kV | 3 | 1.5 | None | 1.6 | 0.8 | 0.8 | 9.9 | 150 | Type 1 · Collectively Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Coll. · 1.1/1.1 kV · 4×1.5 mm² | 1.1/1.1 kV | 4 | 1.5 | None | 1.6 | 0.8 | 0.8 | 10.7 | 200 | Type 1 · Collectively Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Coll. · 1.1/1.1 kV · 6×1.5 mm² | 1.1/1.1 kV | 6 | 1.5 | None | 1.6 | 0.8 | 1 | 12.8 | 250 | Type 1 · Collectively Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Coll. · 1.1/1.1 kV · 16×1.5 mm² | 1.1/1.1 kV | 16 | 1.5 | None | 1.6 | 0.8 | 1.3 | 18.8 | 550 | Type 1 · Collectively Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 1 Coll. · 1.1/1.1 kV · 30×1.5 mm² | 1.1/1.1 kV | 30 | 1.5 | None | 1.6 | 0.8 | 1.5 | 24.7 | 900 | Type 1 · Collectively Screened · 1.1/1.1 kV · V-90/5V-90 PVC
| Type 2S Ind. · 1.1/1.1 kV · 2×10 mm² | 1.1/1.1 kV | 2 | 10 | None | 4.6 | 1 | 1.8 | 18.9 | 600 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 2×16 mm² | 1.1/1.1 kV | 2 | 16 | None | 6.2 | 1 | 1.8 | 22.1 | 850 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 3 | 10 | None | 4.6 | 1 | 1.8 | 20.1 | 750 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 3 | 16 | None | 6.2 | 1 | 1.8 | 23.5 | 1050 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 4×10 mm² | 1.1/1.1 kV | 4 | 10 | None | 4.6 | 1 | 1.8 | 22.1 | 950 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 4×16 mm² | 1.1/1.1 kV | 4 | 16 | None | 6.2 | 1 | 1.8 | 25.9 | 1300 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 2×16 + 1×1P mm² | 1.1/1.1 kV | 2 | 16 | 1 × 1.0 mm² | 6.2 | 1 | 1.8 | 22.1 | 1000 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 2×6 + 2×1P mm² | 1.1/1.1 kV | 2 | 6 | 2 × 1.0 mm² | 3.5 | 1 | 1.8 | 16.9 | 500 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 2×10 + 2×1P mm² | 1.1/1.1 kV | 2 | 10 | 2 × 1.0 mm² | 4.6 | 1 | 1.8 | 19 | 650 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 2×16 + 2×1P mm² | 1.1/1.1 kV | 2 | 16 | 2 × 1.0 mm² | 6.2 | 1 | 1.8 | 22.1 | 900 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 3×6 + 3×1P mm² | 1.1/1.1 kV | 3 | 6 | 3 × 1.0 mm² | 3.5 | 1 | 1.8 | 19.8 | 700 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 3×10 + 3×1P mm² | 1.1/1.1 kV | 3 | 10 | 3 × 1.0 mm² | 4.6 | 1 | 1.8 | 21.3 | 850 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 3×16 + 3×1P mm² | 1.1/1.1 kV | 3 | 16 | 3 × 1.0 mm² | 6.2 | 1 | 1.8 | 23.5 | 1100 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 3×25 + 3×1P mm² | 1.1/1.1 kV | 3 | 25 | 3 × 1.0 mm² | 7.2 | 1.2 | 1.8 | 26.8 | 1550 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 3×35 + 3×1P mm² | 1.1/1.1 kV | 3 | 35 | 3 × 1.0 mm² | 8.4 | 1.2 | 1.8 | 29.5 | 1900 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Ind. · 1.1/1.1 kV · 3×50 + 3×1P mm² | 1.1/1.1 kV | 3 | 50 | 3 × 1.0 mm² | 9.7 | 1.4 | 1.9 | 33.4 | 2450 | Type 2S · Individually Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Coll. · 1.1/1.1 kV · 2×1.5 mm² | 1.1/1.1 kV | 2 | 1.5 | None | 1.6 | 1 | 1.8 | 12.2 | 200 | Type 2S · Collectively Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Coll. · 1.1/1.1 kV · 3×1.5 mm² | 1.1/1.1 kV | 3 | 1.5 | None | 1.6 | 1 | 1.8 | 12.7 | 250 | Type 2S · Collectively Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Coll. · 1.1/1.1 kV · 4×1.5 mm² | 1.1/1.1 kV | 4 | 1.5 | None | 1.6 | 1 | 1.8 | 13.7 | 250 | Type 2S · Collectively Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Coll. · 1.1/1.1 kV · 6×1.5 mm² | 1.1/1.1 kV | 6 | 1.5 | None | 1.6 | 1 | 1.8 | 16 | 350 | Type 2S · Collectively Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Coll. · 1.1/1.1 kV · 16×1.5 mm² | 1.1/1.1 kV | 16 | 1.5 | None | 1.6 | 1 | 1.8 | 22.8 | 750 | Type 2S · Collectively Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S Coll. · 1.1/1.1 kV · 30×1.5 mm² | 1.1/1.1 kV | 30 | 1.5 | None | 1.6 | 1 | 1.8 | 29.1 | 1200 | Type 2S · Collectively Screened · 1.1/1.1 kV · R-EP-90/HD-90-CPE
| Type 2S.3 Ind. · 3.3/3.3 kV · 3×10 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 10 | 3 × 1.5 mm² | 4.6 | 3 | 1.8 | 30.5 | 1400 | Type 2S.3 · Individually Screened · 3.3/3.3 kV · R-EP-90/HD-90-CPE
| Type 2S.3 Ind. · 3.3/3.3 kV · 3×16 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 16 | 3 × 1.5 mm² | 6.2 | 3 | 1.9 | 34.7 | 1850 | Type 2S.3 · Individually Screened · 3.3/3.3 kV · R-EP-90/HD-90-CPE
| Type 2S.3 Ind. · 3.3/3.3 kV · 3×25 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 25 | 3 × 1.5 mm² | 7.2 | 3 | 2 | 37.3 | 2350 | Type 2S.3 · Individually Screened · 3.3/3.3 kV · R-EP-90/HD-90-CPE
| Type 2S.3 Ind. · 3.3/3.3 kV · 3×35 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 35 | 3 × 1.5 mm² | 8.4 | 3 | 2 | 39.8 | 2750 | Type 2S.3 · Individually Screened · 3.3/3.3 kV · R-EP-90/HD-90-CPE
| Type 2S.3 Ind. · 3.3/3.3 kV · 3×50 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 50 | 3 × 1.5 mm² | 9.7 | 3 | 2.1 | 42.8 | 3250 | Type 2S.3 · Individually Screened · 3.3/3.3 kV · R-EP-90/HD-90-CPE
| Type 2S.3 Ind. · 3.3/3.3 kV · 3×70 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 70 | 3 × 1.5 mm² | 12 | 3 | 2.3 | 48.3 | 4350 | Type 2S.3 · Individually Screened · 3.3/3.3 kV · R-EP-90/HD-90-CPE
| Type 2S.3 Ind. · 3.3/3.3 kV · 3×95 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 95 | 3 × 1.5 mm² | 13.3 | 3 | 2.4 | 51.4 | 5150 | Type 2S.3 · Individually Screened · 3.3/3.3 kV · R-EP-90/HD-90-CPE
| Type 2S.3 Ind. · 3.3/3.3 kV · 3×120 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 120 | 3 × 1.5 mm² | 15.3 | 3 | 2.5 | 56.4 | 6400 | Type 2S.3 · Individually Screened · 3.3/3.3 kV · R-EP-90/HD-90-CPE
Type 1 cables have a 5V-90 PVC outer covering and require external mechanical protection (conduit, duct or protective hose) when installed outside enclosures.
Type 2S and Type 2S.3 cables have a heavy-duty HD-90-CPE elastomer outer sheath and do not require further mechanical protection for external non-protected machine interconnections.

## Electrical parameters
AS/NZS 1972 Underground Mining Machine & Feeder Cables – Electrical parameters (43) (43)
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1972-mine-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1972. Values for your order are confirmed in the quotation.
Type · grade · size | Voltage U0/U | Main cores | Core area (mm²) | AC resistance 90 °C (Ω/km) | Reactance 50 Hz (Ω/km) | Voltage drop (mV/A·m) | Max. DC res. combined (Ω/km) | Series
Type 1 Ind. · 1.1/1.1 kV · 2×1.5 mm² | 1.1/1.1 kV | 2 | 1.5 | 17.5 | 0.12 | 30.3 | 13.7 | Type 1 · Individually Screened · 1.1/1.1 kV
Type 1 Ind. · 1.1/1.1 kV · 3×1.5 mm² | 1.1/1.1 kV | 3 | 1.5 | 17.5 | 0.12 | 30.3 | 13.7 | Type 1 · Individually Screened · 1.1/1.1 kV
Type 1 Ind. · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 3 | 10 | 2.58 | 0.0923 | 4.47 | 6.06 | Type 1 · Individually Screened · 1.1/1.1 kV
Type 1 Ind. · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 3 | 16 | 1.58 | 0.0854 | 2.74 | 3.72 | Type 1 · Individually Screened · 1.1/1.1 kV
Type 1 Ind. · 1.1/1.1 kV · 4×1.5 mm² | 1.1/1.1 kV | 4 | 1.5 | 17.5 | 0.128 | 30.3 | 13.7 | Type 1 · Individually Screened · 1.1/1.1 kV
Type 1 Ind. · 1.1/1.1 kV · 4×10 mm² | 1.1/1.1 kV | 4 | 10 | 2.58 | 0.0998 | 4.47 | 6.06 | Type 1 · Individually Screened · 1.1/1.1 kV
Type 1 Ind. · 1.1/1.1 kV · 4×16 mm² | 1.1/1.1 kV | 4 | 16 | 1.58 | 0.0929 | 2.74 | 3.72 | Type 1 · Individually Screened · 1.1/1.1 kV
Type 1 Coll. · 1.1/1.1 kV · 2×1.5 mm² | 1.1/1.1 kV | 2 | 1.5 | 17.5 | 0.106 | 30.3 | 13.7 | Type 1 · Collectively Screened · 1.1/1.1 kV
Type 1 Coll. · 1.1/1.1 kV · 3×1.5 mm² | 1.1/1.1 kV | 3 | 1.5 | 17.5 | 0.106 | 30.3 | 13.7 | Type 1 · Collectively Screened · 1.1/1.1 kV
Type 1 Coll. · 1.1/1.1 kV · 4×1.5 mm² | 1.1/1.1 kV | 4 | 1.5 | 17.5 | 0.114 | 30.3 | 13.7 | Type 1 · Collectively Screened · 1.1/1.1 kV
Type 1 Coll. · 1.1/1.1 kV · 6×1.5 mm² | 1.1/1.1 kV | 6 | 1.5 | 17.5 | 0.123 | 30.3 | 13.7 | Type 1 · Collectively Screened · 1.1/1.1 kV
Type 1 Coll. · 1.1/1.1 kV · 16×1.5 mm² | 1.1/1.1 kV | 16 | 1.5 | 17.5 | 0.152 | 30.3 | 13.7 | Type 1 · Collectively Screened · 1.1/1.1 kV
Type 1 Coll. · 1.1/1.1 kV · 30×1.5 mm² | 1.1/1.1 kV | 30 | 1.5 | 17.5 | 0.169 | 30.3 | 13.7 | Type 1 · Collectively Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 2×10 mm² | 1.1/1.1 kV | 2 | 10 | 2.58 | 0.0953 | 4.47 | 6.06 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 2×16 mm² | 1.1/1.1 kV | 2 | 16 | 1.58 | 0.0879 | 2.74 | 3.72 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 3×10 mm² | 1.1/1.1 kV | 3 | 10 | 2.58 | 0.0953 | 4.47 | 6.06 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 3×16 mm² | 1.1/1.1 kV | 3 | 16 | 1.58 | 0.0879 | 2.74 | 3.72 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 4×10 mm² | 1.1/1.1 kV | 4 | 10 | 2.58 | 0.103 | 4.47 | 6.06 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 4×16 mm² | 1.1/1.1 kV | 4 | 16 | 1.58 | 0.0954 | 2.74 | 3.72 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 2×16 + 1×1P mm² | 1.1/1.1 kV | 2 | 16 | 1.58 | 0.0786 | 2.74 | 3.72 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 2×6 + 2×1P mm² | 1.1/1.1 kV | 2 | 6 | 4.32 | 0.0936 | 7.48 | 8.21 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 2×10 + 2×1P mm² | 1.1/1.1 kV | 2 | 10 | 2.58 | 0.086 | 4.47 | 6.06 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 2×16 + 2×1P mm² | 1.1/1.1 kV | 2 | 16 | 1.58 | 0.0786 | 2.74 | 3.72 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 3×6 + 3×1P mm² | 1.1/1.1 kV | 3 | 6 | 4.32 | 0.119 | 7.49 | 8.21 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 3×10 + 3×1P mm² | 1.1/1.1 kV | 3 | 10 | 2.58 | 0.104 | 4.47 | 6.06 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 3×16 + 3×1P mm² | 1.1/1.1 kV | 3 | 16 | 1.58 | 0.0879 | 2.74 | 3.72 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 3×25 + 3×1P mm² | 1.1/1.1 kV | 3 | 25 | 0.951 | 0.087 | 1.65 | 2.24 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 3×35 + 3×1P mm² | 1.1/1.1 kV | 3 | 35 | 0.698 | 0.0837 | 1.22 | 1.64 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Ind. · 1.1/1.1 kV · 3×50 + 3×1P mm² | 1.1/1.1 kV | 3 | 50 | 0.523 | 0.0828 | 0.917 | 1.23 | Type 2S · Individually Screened · 1.1/1.1 kV
Type 2S Coll. · 1.1/1.1 kV · 2×1.5 mm² | 1.1/1.1 kV | 2 | 1.5 | 17.5 | 0.118 | 30.3 | 13.7 | Type 2S · Collectively Screened · 1.1/1.1 kV
Type 2S Coll. · 1.1/1.1 kV · 3×1.5 mm² | 1.1/1.1 kV | 3 | 1.5 | 17.5 | 0.119 | 30.3 | 13.7 | Type 2S · Collectively Screened · 1.1/1.1 kV
Type 2S Coll. · 1.1/1.1 kV · 4×1.5 mm² | 1.1/1.1 kV | 4 | 1.5 | 17.5 | 0.126 | 30.3 | 13.7 | Type 2S · Collectively Screened · 1.1/1.1 kV
Type 2S Coll. · 1.1/1.1 kV · 6×1.5 mm² | 1.1/1.1 kV | 6 | 1.5 | 17.5 | 0.135 | 30.3 | 13.7 | Type 2S · Collectively Screened · 1.1/1.1 kV
Type 2S Coll. · 1.1/1.1 kV · 16×1.5 mm² | 1.1/1.1 kV | 16 | 1.5 | 17.5 | 0.164 | 30.3 | 13.7 | Type 2S · Collectively Screened · 1.1/1.1 kV
Type 2S Coll. · 1.1/1.1 kV · 30×1.5 mm² | 1.1/1.1 kV | 30 | 1.5 | 17.5 | 0.181 | 30.3 | 13.7 | Type 2S · Collectively Screened · 1.1/1.1 kV
Type 2S.3 Ind. · 3.3/3.3 kV · 3×10 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 10 | 2.58 | 0.125 | 4.47 | 6.06 | Type 2S.3 · Individually Screened · 3.3/3.3 kV
Type 2S.3 Ind. · 3.3/3.3 kV · 3×16 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 16 | 1.58 | 0.116 | 2.74 | 3.72 | Type 2S.3 · Individually Screened · 3.3/3.3 kV
Type 2S.3 Ind. · 3.3/3.3 kV · 3×25 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 25 | 0.951 | 0.11 | 1.66 | 2.24 | Type 2S.3 · Individually Screened · 3.3/3.3 kV
Type 2S.3 Ind. · 3.3/3.3 kV · 3×35 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 35 | 0.698 | 0.105 | 1.22 | 1.64 | Type 2S.3 · Individually Screened · 3.3/3.3 kV
Type 2S.3 Ind. · 3.3/3.3 kV · 3×50 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 50 | 0.523 | 0.101 | 0.923 | 1.23 | Type 2S.3 · Individually Screened · 3.3/3.3 kV
Type 2S.3 Ind. · 3.3/3.3 kV · 3×70 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 70 | 0.346 | 0.095 | 0.621 | 0.813 | Type 2S.3 · Individually Screened · 3.3/3.3 kV
Type 2S.3 Ind. · 3.3/3.3 kV · 3×95 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 95 | 0.271 | 0.0926 | 0.496 | 0.636 | Type 2S.3 · Individually Screened · 3.3/3.3 kV
Type 2S.3 Ind. · 3.3/3.3 kV · 3×120 + 3×1.5P mm² | 3.3/3.3 kV | 3 | 120 | 0.21 | 0.0897 | 0.396 | 0.492 | Type 2S.3 · Individually Screened · 3.3/3.3 kV
Cables rated in excess of 20 A are electrically symmetrical per AS/NZS 1972.
'Max. DC res. combined (Ω/km)' specifies the maximum combined DC resistance at 20 °C of the composite earth screen (plus any earth conductor) for fault-loop impedance verification.

## Technical data
AS/NZS 1972 Underground Mining Machine & Feeder Cables – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1972-mine-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1972. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.1 & 3.3 kV (1.1/1.1 kV (1, 2S) · 3.3/3.3 kV (2S.3))
Key data | Conductor size | 1.5–120 mm² (2 to 30 cores · tinned copper)
Key data | Conductor temp. | +90 °C (Max. continuous (V-90 & R-EP-90))
Key data | Min. temp. | −25 °C / 0 °C (−25 °C Type 2S · 0 °C Type 1)
Key data | Flame rating | Cat. C1 / C3 (C1 (Type 2S/2S.3) · C3 (Type 1))
Key data | Screen design | Ind. or Coll. (Composite tinned copper / polyester)
Electrical | Rated voltage U0/U | 1.1/1.1 kV (Types 1 & 2S); 3.3/3.3 kV (Type 2S.3)
Electrical | Screening configurations | Individually screened (2–4C) or collectively screened (2–30C)
Electrical | Electrical symmetry | Cables rated > 20 A are electrically symmetrical
Electrical | Pilot conductors (Type 2S/2S.3) | Optional 1, 2 or 3 × 1.0 mm² (2S); 3 × 1.5 mm² (2S.3)
Thermal | Max. continuous conductor temp. | +90 °C (V-90 PVC on Type 1; R-EP-90 EPR on Type 2S)
Thermal | Short-circuit temperature | +250 °C (R-EP-90 Type 2S); +160 °C (V-90 PVC Type 1)
Thermal | Min. installation temperature | −25 °C (Type 2S / 2S.3); 0 °C (Type 1 PVC)
Mechanical | Conductor stranding | Flexible stranded tinned annealed copper (AS/NZS 1125)
Mechanical | External protection requirement | Type 1 requires duct/hose; Type 2S self-protected in free air
Mechanical | Minimum bend radius | 6 × D fixed machine wiring; 10 × D flexing interconnect
Resistance | Flame retardance | AS/NZS 1660.5.6 Cat. C1 (Type 2S/2S.3) & Cat. C3 (Type 1)
Resistance | Oil & water performance | Immersion resistant (Type 2S HD-90-CPE); splash resistant (Type 1)
Standards | Primary design standard | AS/NZS 1972 (underground coal mining — non-reeling/trailing)
Standards | Compounds & conductors | AS/NZS 3808 (V-90, 5V-90, R-EP-90, HD-90-CPE); AS/NZS 1125
Identification | Insulation & sheath materials | Type 1: V-90 / 5V-90 PVC; Type 2S: R-EP-90 EPR / HD-90-CPE
Identification | Outer sheath colour | Black heavy-duty HD-90-CPE (Type 2S/2S.3) or 5V-90 PVC (Type 1)

## Construction
AS/NZS 1972 Underground Mining Machine & Feeder Cables – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1972-mine-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1972. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible tinned copper conductor | Flexible stranded tinned annealed copper conductor per AS/NZS 1125 | AS/NZS 1125
2 | 90 °C core insulation (R-EP-90 EPR or V-90 PVC) | Thermoset ethylene propylene rubber (R-EP-90 on Types 2S & 2S.3) or heat-resistant V-90 PVC (on Type 1) per AS/NZS 3808 | AS/NZS 3808
3 | Composite tinned copper / polyester earth screen | Tinned annealed copper wire interwoven with polyester yarn applied over each individual core (2–4C) or collectively over the laid-up bundle (2–30C) | AS/NZS 1972
4 | Interstitial pilot conductors (Type 2S & Type 2S.3) | Optional 1, 2 or 3 × 1.0 mm² (Type 2S) or 3 × 1.5 mm² (Type 2S.3) R-EP-90 insulated tinned copper pilot cores | AS/NZS 1972
5 | Outer sheath / covering (HD-90-CPE or 5V-90 PVC) | Heavy-duty black chlorinated polyethylene elastomer (HD-90-CPE on Types 2S & 2S.3, Cat. C1) or heat-resistant 5V-90 PVC covering (on Type 1, Cat. C3) | AS/NZS 3808
| Type 1 · 1.1/1.1 kV (V-90 / 5V-90 PVC) | Compact PVC-insulated and PVC-covered screened machine cable (individually or collectively screened) for routing inside machine ducts or protective conduit.
| Type 2S · 1.1/1.1 kV (R-EP-90 EPR / HD-90-CPE) | Elastomer-insulated and heavy-duty CPE-sheathed cable with optional 1–3 pilot cores; approved for external non-protected machine interconnect and longwall lighting.
| Type 2S.3 · 3.3/3.3 kV (R-EP-90 EPR / HD-90-CPE + 3 Pilots) | Medium-voltage 3.3/3.3 kV individually screened three-core + 3 × 1.5 mm² pilot cable for high-power cutter-head and pump motor interconnections.

## Series
AS/NZS 1972 Underground Mining Machine & Feeder Cables – Series
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1972-mine-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1972. Values for your order are confirmed in the quotation.
Code | Series | Rating | Standard / class | Sizes | Typical use
Type 1 Ind. | Type 1 Individually Screened | 1.1/1.1 kV | V-90 / 5V-90 PVC | 7 | Protected onboard wiring between control boxes and motors
Type 1 Coll. | Type 1 Collectively Screened | 1.1/1.1 kV | V-90 / 5V-90 PVC | 6 | Multi-core control & pilot wiring inside machine enclosures
Type 2S Ind. | Type 2S Individually Screened | 1.1/1.1 kV | R-EP-90 / HD-90-CPE | 16 | Exposed motor interconnections & longwall lighting systems
Type 2S Coll. | Type 2S Collectively Screened | 1.1/1.1 kV | R-EP-90 / HD-90-CPE | 6 | Unprotected multi-core control & solenoid interconnections
Type 2S.3 | Type 2S.3 Individually Screened | 3.3/3.3 kV | R-EP-90 / HD-90-CPE | 8 | 3.3 kV cutter-head, traction and pump motor leads onboard miners

## Quality and supply
AS/NZS 1972 Underground Mining Machine & Feeder Cables – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/as-nzs-1972-mine-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AS/NZS 1972. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor & composite earth-screen DC resistance test — 100 % drum verification of phase conductor DC resistance (AS/NZS 1125) and combined earth-screen DC resistance per AS/NZS 1972 | Every production length
Routine test | High-voltage AC dielectric withstand test — 5-minute AC voltage test on all insulated cores (3.5 kV for 1.1/1.1 kV; 6.5 kV for 3.3/3.3 kV) per AS/NZS 1972 | Every production length
Type test | Flame propagation (AS/NZS 1660.5.6 Category C1 / C3) — Category C1 vertical flame test on Type 2S / 2S.3 (HD-90-CPE) and Category C3 on Type 1 (5V-90 PVC) | Type approval & periodic sample
Standard / approval | AS/NZS 1972 Underground Coal Mining Machine & Interconnect Cable
Standard / approval | AS/NZS 1660.5.6 Category C1 (Type 2S/2S.3) & Category C3 (Type 1)
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX — AS/NZS 1972 — TYPE <1 / 2S / 2S.3> — <1.1/1.1 OR 3.3/3.3 kV> — <CORES × AREA mm²> — SCREENED — YEAR — METRE MARK
Supply | Standard packing: 250 m, 500 m or 1,000 m wooden drums; custom machine-kit cut lengths
Supply | Screening options: Individually screened power cores (2–4C) or collectively screened control cores (2–30C)
Supply | Export tariff code: HS 8544.60 (> 1,000 V screened mining cables)