## Request a quote
Request a quotation for BFOU(I) S3/S7 & BFOU(C) S4/S8 250 V
Share pair/triad/quad count, conductor size (mm² or AWG), collective vs. individual+collective screen (c/i or OS/IS) and sheath grade.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bfou-i-s3-s7-bfou-c-s4-s8-250-v/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
BFOU(i) S3/S7 & BFOU(c) S4/S8 250 V NEK 606 Fire-Resistant Offshore In – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bfou-i-s3-s7-bfou-c-s4-s8-250-v/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| BFOU(I) S3 2×2×0.75 mm² | 2 × 2 × 0.75 mm² (2Pr) | Stranded Cu/SnCu (IEC 60228 Class 2/5) | 11.4 | 195 | 1.2 | 70 | BFOU(I) S3/S7 & BFOU(C) S4/S8 250 V Construction Schedule (−40…+90 °C)
| BFOU(I) S3 4×2×1.0 mm² | 4 × 2 × 1.0 mm² (4Pr) | Stranded Cu/SnCu (IEC 60228 Class 2/5) | 15.6 | 365 | 2.4 | 95 | BFOU(I) S3/S7 & BFOU(C) S4/S8 250 V Construction Schedule (−40…+90 °C)
| BFOU(I) S3 8×2×1.5 mm² | 8 × 2 × 1.5 mm² (8Pr) | Stranded Cu/SnCu (IEC 60228 Class 2/5) | 22.8 | 760 | 4.8 | 140 | BFOU(I) S3/S7 & BFOU(C) S4/S8 250 V Construction Schedule (−40…+90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331.

## Electrical, optical & thermal p
BFOU(i) S3/S7 & BFOU(c) S4/S8 250 V NEK 606 Fire-Resistant Offshore In – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bfou-i-s3-s7-bfou-c-s4-s8-250-v/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
2 × 2 × 0.75 mm² (2Pr) | 26 | 150/250 V (≤60 nF/km) | −40…+90 °C
4 × 2 × 1.0 mm² (4Pr) | 19.5 | 150/250 V (≤65 nF/km) | −40…+90 °C
8 × 2 × 1.5 mm² (8Pr) | 13.3 | 150/250 V (≤75 nF/km) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
BFOU(i) S3/S7 & BFOU(c) S4/S8 250 V NEK 606 Fire-Resistant Offshore In – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bfou-i-s3-s7-bfou-c-s4-s8-250-v/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 150/250 V (Tested per NEK TS 606 / IEC 60092-376)
Key data | Operating temp. | −40…+90 °C (Continuous shipboard & offshore service)
Key data | Min. bend radius | 8 × OD (Marine tray, bulkhead & deck routing)
Key data | Core / conductor | Mica + EPR Twist (Tinned copper conductors with mica fire )
Key data | Outer protection | Blue Ex-i / Grey (Mud-resistant thermoset outer sheath (Bl)
Key data | Standard | NEK TS 606 / IEC (NEK TS 606 Code S3/S7/S103 & S4/S8/S104 )
Electrical | Rated voltage / transmission duty | 150/250 V (NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331)
Electrical | Core / conductor construction | Mica + EPR Twisted Pairs (8×2×1.0 mm²) — Tinned copper conductors with mica fire tape and Black/White EPR insulation
Electrical | Primary dielectric / buffering | Individual Pair Foil Screen (BFOU(i)) — Color-coded/numbered Al/PET foil tape + tinned copper drain wire per pair
Thermal | Continuous operating temperature | −40…+90 °C (shipboard & offshore duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Blue Ex-i / Grey SHF2-MUD Jacket (S3/S7) — Mud-resistant thermoset outer sheath (Blue for Intrinsically Safe circuits)
Mechanical | Minimum bending radius | 8 × OD
Mechanical | Armour, screen & mechanical duty | Tinned Copper Braid Armour (TCWB) — High-coverage tinned copper wire braid screen and armour
Resistance | Flame, fire & smoke performance | Qualified for marine flame-retardance and low-smoke zero-halogen / fire safety per NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331
Resistance | Oil, drilling mud & seawater resistance | Resistant to marine fuel/lube oils, salt mist and offshore fluids per NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331
Standards | Environmental & test standards | IEC 60228 / IEC 60332-3-22 / IEC 60754 / IEC 61034 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | BFOU(I) S3/S7 & BFOU(C) S4/S8 250 V
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Blue Ex-i / Grey)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
BFOU(i) S3/S7 & BFOU(c) S4/S8 250 V NEK 606 Fire-Resistant Offshore In – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bfou-i-s3-s7-bfou-c-s4-s8-250-v/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Mica + EPR Twisted Pairs (8×2×1.0 mm²) | Tinned copper conductors with mica fire tape and Black/White EPR insulation
2 | Individual Pair Foil Screen (BFOU(i)) | Color-coded/numbered Al/PET foil tape + tinned copper drain wire per pair
3 | SHF2 Elastomeric Inner Bedding | Flame-retardant halogen-free thermoset inner sheath
4 | Tinned Copper Braid Armour (TCWB) | High-coverage tinned copper wire braid screen and armour
5 | Blue Ex-i / Grey SHF2-MUD Jacket (S3/S7) | Mud-resistant thermoset outer sheath (Blue for Intrinsically Safe circuits)
| BFOU(I) S3/S7 & BFOU(C) S4/S8 250 V — Standard Shipboard & Offshore Execution | Built to NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331 with mica + epr twisted pairs (8×2×1.0 mm²) and blue ex-i / grey shf2-mud jacket (s3/s7)
| BFOU(I) S3/S7 & BFOU(C) S4/S8 250 V — Custom Drum Length & Gland Kit | Available in custom continuous shipboard/offshore drum lengths or with marine EMC cable glands
| BFOU(I) S3/S7 & BFOU(C) S4/S8 250 V — Class & Routine Test Certified | Supplied with EN 10204 3.1 routine dielectric, conductor resistance & flame/fire test report

## Quality and supply
BFOU(i) S3/S7 & BFOU(c) S4/S8 250 V NEK 606 Fire-Resistant Offshore In – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bfou-i-s3-s7-bfou-c-s4-s8-250-v/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331) — DC resistance at 20 °C / optical attenuation and outer diameter within NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331) — Zero dielectric breakdown and verified insulation resistance for 150/250 V rating | Every manufactured drum length
Type test | Flame, fire integrity, oil/mud & mechanical qualification (NEK TS 606 Code S3/S7/S103 & S4/S8/S104 / IEC 60092-376 / IEC 60331) — Verified flame/fire performance, fluid resistance and thermal stability across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | NEK TS 606 / IEC 60092-376 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BFOU(I) S3/S7 & BFOU(C) S4/S8 250 V NEK TS 606 / IEC 60092-376 150/250 V CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel marine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shipboard/offshore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP