## Request a quote
Request a quotation for BRUsens DTS AHFO
Application engineer · optical & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/brusens-dts-ahfo-distributed-temperature-sensing-fibre-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BRUsens DTS AHFO Distributed Temperature Sensing Fibre Cable – Dimensions & thermal ratings (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/brusens-dts-ahfo-distributed-temperature-sensing-fibre-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60794-2-20 / IEC 61757-2-2 / EN 54-22. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Fibre compliment | Outer Ø mm | Weight ≈ kg/km | Max. pull N | Max. temp °C | Series
| BRUsens DTS AHFO-02MM | 2 × 50/125 OM3 MM · LSZH | 4 | 16 | 800 | 85 | All-Dielectric Halogen-Free DTS Cables
| BRUsens DTS AHFO-04MM | 4 × 50/125 OM3 MM · LSZH | 4.5 | 21 | 1000 | 85 | All-Dielectric Halogen-Free DTS Cables
| BRUsens DTS AHFO-02MM02SM | 2 × OM3 MM + 2 × G.657.A1 SM · LSZH | 4.5 | 21 | 1000 | 85 | All-Dielectric Halogen-Free DTS Cables
| BRUsens DTS AHFO-HT-04HYB | 2 × OM3 + 2 × SM · +125 °C TPEE | 4.8 | 25 | 1200 | 125 | All-Dielectric Halogen-Free DTS Cables
All models are 100 % non-metallic and safe for direct contact with high-voltage power cables and busbars.

## Technical data
BRUsens DTS AHFO Distributed Temperature Sensing Fibre Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/brusens-dts-ahfo-distributed-temperature-sensing-fibre-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60794-2-20 / IEC 61757-2-2 / EN 54-22. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Sensing mode | Raman / BOTDA (OM3 multimode + SM fibres)
Key data | Dielectric | 100 % Metal-Free (Safe on HV cable sheaths)
Key data | Outer Ø | 4.0 to 5.2 mm (Fast thermal time constant)
Key data | Temperature | -40 to +85 °C (+125 °C TPEE jacket option)
Key data | Tensile load | 600 to 1,200 N (Aramid / FRP reinforcement)
Key data | Flame rating | IEC 60332-3-24 (Low-smoke zero-halogen)
Electrical | Dielectric design | 100 % metal-free all-dielectric (no grounding needed)
Electrical | Sensing principle | Raman OTDR (MM) & Brillouin BOTDA (SM)
Electrical | HV sheath strapping | Zero induced circulating current on 66–500 kV cables
Thermal | Operating temperature | -40 °C to +85 °C (LSZH) · -40 °C to +125 °C (HT)
Thermal | Thermal response (τ₆₃) | ≤ 2.5 s in water · ≤ 8.0 s in moving air
Thermal | Installation temperature | -15 °C to +60 °C
Mechanical | Outer diameter | 4.0 mm to 5.2 mm
Mechanical | Max. tensile load | 800 N (standard) · 1,200 N (reinforced)
Mechanical | Crush resistance | 1,200 N / 100 mm
Mechanical | Min. bend radius | 10 × OD static · 15 × OD dynamic
Optical | Multimode DTS fibres | 50/125 µm OM3 bend-insensitive (IEC 60793-2-10 A1a.2)
Optical | Attenuation (OM3) | ≤ 2.4 dB/km @ 850 nm · ≤ 0.6 dB/km @ 1300 nm
Optical | Single-mode fibres | ITU-T G.657.A1 (≤ 0.35 / 0.21 dB/km @ 1310/1550 nm)
Resistance | Flame propagation | IEC 60332-1-2 & IEC 60332-3-24 Cat C
Resistance | Halogen-free & smoke | IEC 60754-1/2 (pH ≥ 4.3) & IEC 61034-2 (≥ 60 %)
Resistance | Water blocking | Dry water-swellable yarns per IEC 60794-1-22 F5B
Standards | DTS sensor standard | IEC 61757-2-2 & EN 54-22 Linear Heat Detection
Standards | Cable standard | IEC 60794-2-20 Indoor/Outdoor Optical Cables
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Outer sheath colour | Red (Fire/LHD), Orange, or Black LSZH
Identification | Fibre colour code | TIA-598-D 12-colour
Identification | Customs tariff (HS) | 8544.7000

## Construction
BRUsens DTS AHFO Distributed Temperature Sensing Fibre Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/brusens-dts-ahfo-distributed-temperature-sensing-fibre-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60794-2-20 / IEC 61757-2-2 / EN 54-22. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Strain-free DTS sensing fibres | 2 or 4 × 50/125 µm OM3 graded-index multimode fibres (plus optional 2 × G.657.A1 SM fibres)
2 | High-thermal-conductivity buffer tube | Thin-wall dry PBT/TPEE micro-tube providing controlled excess fibre length (EFL)
3 | All-dielectric aramid & glass yarn | High-modulus polyaramid and E-glass yarns with dry water-blocking swellable yarn
4 | Halogen-free LSZH / TPEE outer jacket | Flame-retardant LSZH (IEC 60332-3-24, IEC 60754-2, IEC 61034-2) or +125 °C TPEE
| BRUsens DTS AHFO-LSZH (-40/+85 °C) | Ø 4.5 mm all-dielectric LSZH cable for HV power cables, tunnels and BESS racks
| BRUsens DTS AHFO-HT (-40/+125 °C) | Ø 4.8 mm high-temperature halogen-free TPEE jacket for busducts and transformer windings

## Quality and supply
BRUsens DTS AHFO Distributed Temperature Sensing Fibre Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/brusens-dts-ahfo-distributed-temperature-sensing-fibre-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60794-2-20 / IEC 61757-2-2 / EN 54-22. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % bidirectional OTDR attenuation test — ≤ 2.4 / 0.6 dB/km (OM3) and ≤ 0.35 / 0.21 dB/km (SM) | Every drum length
Type test | Thermal step response & cycling test — Zero excess attenuation across -40 to +85/+125 °C; τ₆₃ ≤ 2.5 s in water | Type qualification
Type test | Bunched flame, smoke & halogen-free test — Pass IEC 60332-3-24, IEC 60754-2 and IEC 61034-2 | Type qualification
Standard / approval | IEC 61757-2-2 & EN 54-22 LHD
Standard / approval | IEC 60332-3-24 & IEC 60754-2 LSZH
Standard / approval | RoHS 2 & REACH Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BRUSENS DTS AHFO METAL-FREE LSZH IEC 60332-3
Supply | Delivery form: Fumigated export wooden or steel drums
Supply | Standard drum lengths: 1000 m · 2000 m · 4000 m (or custom cut lengths)
Supply | MOQ: 500 m (standard) · 1000 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP