## Request a quote
Request a quotation for BS 6195 Type 4A / 4C / 4D
Application engineer · HV/LV machine leads & festoon cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6195-type-4a-4c-4d-flexible-coil-lead-and-festoon-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6195 Type 4A / 4C / 4D Flexible Coil-Lead and Festoon Cable – Dimensions & weights (20)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6195-type-4a-4c-4d-flexible-coil-lead-and-festoon-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6195. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation Type 4A (90 °C EPR/CSP) | Order designation Type 4D (110 °C EVA) | Order designation Type 4C (150 °C Silicone) | Category & U0/U | Cores × mm² | Nominal wall mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| BS 6195 Type 4A Cat.2 1×2.5 | BS 6195 Type 4D Cat.2 1×2.5 | BS 6195 Type 4C Cat.2 1×2.5 | Cat.2 · 0.6/1 kV | 1 × 2.5 | 1.4 | 5.5 | 24 | 48 | 33 | Category 2 · 600/1000 V
| BS 6195 Type 4A Cat.2 1×6 | BS 6195 Type 4D Cat.2 1×6 | BS 6195 Type 4C Cat.2 1×6 | Cat.2 · 0.6/1 kV | 1 × 6 | 1.6 | 7.4 | 58 | 98 | 44 | Category 2 · 600/1000 V
| BS 6195 Type 4A Cat.2 1×16 | BS 6195 Type 4D Cat.2 1×16 | BS 6195 Type 4C Cat.2 1×16 | Cat.2 · 0.6/1 kV | 1 × 16 | 1.8 | 10.2 | 154 | 215 | 61 | Category 2 · 600/1000 V
| BS 6195 Type 4A Cat.2 1×35 | BS 6195 Type 4D Cat.2 1×35 | BS 6195 Type 4C Cat.2 1×35 | Cat.2 · 0.6/1 kV | 1 × 35 | 2 | 13.4 | 336 | 430 | 80 | Category 2 · 600/1000 V
| BS 6195 Type 4A Cat.2 1×70 | BS 6195 Type 4D Cat.2 1×70 | BS 6195 Type 4C Cat.2 1×70 | Cat.2 · 0.6/1 kV | 1 × 70 | 2.2 | 17.5 | 672 | 810 | 105 | Category 2 · 600/1000 V
| BS 6195 Type 4A Cat.2 1×120 | BS 6195 Type 4D Cat.2 1×120 | BS 6195 Type 4C Cat.2 1×120 | Cat.2 · 0.6/1 kV | 1 × 120 | 2.4 | 21.6 | 1152 | 1340 | 130 | Category 2 · 600/1000 V
| BS 6195 Type 4A Cat.2 1×240 | BS 6195 Type 4D Cat.2 1×240 | BS 6195 Type 4C Cat.2 1×240 | Cat.2 · 0.6/1 kV | 1 × 240 | 2.8 | 29.2 | 2304 | 2610 | 175 | Category 2 · 600/1000 V
| BS 6195 Type 4A Cat.3 1×16 | BS 6195 Type 4D Cat.3 1×16 | BS 6195 Type 4C Cat.3 1×16 | Cat.3 · 1.9/3.3 kV | 1 × 16 | 3.2 | 13 | 154 | 285 | 78 | Category 3 · 1900/3300 V
| BS 6195 Type 4A Cat.3 1×35 | BS 6195 Type 4D Cat.3 1×35 | BS 6195 Type 4C Cat.3 1×35 | Cat.3 · 1.9/3.3 kV | 1 × 35 | 3.2 | 15.8 | 336 | 510 | 95 | Category 3 · 1900/3300 V
| BS 6195 Type 4A Cat.3 1×70 | BS 6195 Type 4D Cat.3 1×70 | BS 6195 Type 4C Cat.3 1×70 | Cat.3 · 1.9/3.3 kV | 1 × 70 | 3.2 | 19.6 | 672 | 910 | 118 | Category 3 · 1900/3300 V
| BS 6195 Type 4A Cat.3 1×120 | BS 6195 Type 4D Cat.3 1×120 | BS 6195 Type 4C Cat.3 1×120 | Cat.3 · 1.9/3.3 kV | 1 × 120 | 3.2 | 23.4 | 1152 | 1450 | 140 | Category 3 · 1900/3300 V
| BS 6195 Type 4A Cat.3 1×240 | BS 6195 Type 4D Cat.3 1×240 | BS 6195 Type 4C Cat.3 1×240 | Cat.3 · 1.9/3.3 kV | 1 × 240 | 3.4 | 30.6 | 2304 | 2740 | 184 | Category 3 · 1900/3300 V
| BS 6195 Type 4A Cat.4 1×25 | BS 6195 Type 4D Cat.4 1×25 | BS 6195 Type 4C Cat.4 1×25 | Cat.4 · 3.8/6.6 kV | 1 × 25 | 5 | 18.2 | 240 | 490 | 109 | Category 4 · 3800/6600 V
| BS 6195 Type 4A Cat.4 1×50 | BS 6195 Type 4D Cat.4 1×50 | BS 6195 Type 4C Cat.4 1×50 | Cat.4 · 3.8/6.6 kV | 1 × 50 | 5 | 21.4 | 480 | 790 | 128 | Category 4 · 3800/6600 V
| BS 6195 Type 4A Cat.4 1×95 | BS 6195 Type 4D Cat.4 1×95 | BS 6195 Type 4C Cat.4 1×95 | Cat.4 · 3.8/6.6 kV | 1 × 95 | 5 | 25.4 | 912 | 1310 | 152 | Category 4 · 3800/6600 V
| BS 6195 Type 4A Cat.4 1×185 | BS 6195 Type 4D Cat.4 1×185 | BS 6195 Type 4C Cat.4 1×185 | Cat.4 · 3.8/6.6 kV | 1 × 185 | 5 | 30.8 | 1776 | 2290 | 185 | Category 4 · 3800/6600 V
| BS 6195 Type 4A Cat.5 1×35 | BS 6195 Type 4D Cat.5 1×35 | BS 6195 Type 4C Cat.5 1×35 | Cat.5 · 6.35/11 kV | 1 × 35 | 7.6 | 24.8 | 336 | 890 | 149 | Category 5 · 6350/11000 V
| BS 6195 Type 4A Cat.5 1×70 | BS 6195 Type 4D Cat.5 1×70 | BS 6195 Type 4C Cat.5 1×70 | Cat.5 · 6.35/11 kV | 1 × 70 | 7.6 | 28.4 | 672 | 1340 | 170 | Category 5 · 6350/11000 V
| BS 6195 Type 4A Cat.5 1×120 | BS 6195 Type 4D Cat.5 1×120 | BS 6195 Type 4C Cat.5 1×120 | Cat.5 · 6.35/11 kV | 1 × 120 | 7.6 | 32.2 | 1152 | 1920 | 193 | Category 5 · 6350/11000 V
| BS 6195 Type 4A Cat.5 1×240 | BS 6195 Type 4D Cat.5 1×240 | BS 6195 Type 4C Cat.5 1×240 | Cat.5 · 6.35/11 kV | 1 × 240 | 7.6 | 39 | 2304 | 3280 | 234 | Category 5 · 6350/11000 V
Other BS 6195 cross-sections from 1.5 mm² up to 630 mm² across Categories 2, 3, 4 and 5 are manufactured to order.
Type 4A (90 °C EPR/CSP), Type 4D (110 °C EVA) and Type 4C (150 °C Silicone + glass braid) share identical BS 6195 radial wall thicknesses per category.

## Electrical & current data by cr
BS 6195 Type 4A / 4C / 4D Flexible Coil-Lead and Festoon Cable – Electrical & current data by cross-section (11)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6195-type-4a-4c-4d-flexible-coil-lead-and-festoon-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6195. Values for your order are confirmed in the quotation.
Conductor CSA mm² | Max. DC resistance 20 °C, Ω/km | Type 4A (90 °C) A in air | Type 4D (110 °C) A in air | Type 4C (150 °C) A in air
2.5 | 8.21 | 36 | 42 | 52
6 | 3.39 | 63 | 73 | 90
16 | 1.24 | 115 | 133 | 165
25 | 0.795 | 152 | 176 | 218
35 | 0.565 | 188 | 218 | 270
50 | 0.393 | 234 | 271 | 335
70 | 0.277 | 292 | 338 | 418
95 | 0.21 | 354 | 410 | 506
120 | 0.164 | 412 | 478 | 590
185 | 0.108 | 540 | 626 | 772
240 | 0.0817 | 642 | 744 | 918
Current ratings are for a single cable in free air at 30 °C ambient; apply derating when bundled inside motor terminal boxes or enclosed ducts.

## Technical data
BS 6195 Type 4A / 4C / 4D Flexible Coil-Lead and Festoon Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6195-type-4a-4c-4d-flexible-coil-lead-and-festoon-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6195. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage grades | 0.6/1–6.35/11 kV (Cat. 2 (1 kV), 3 (3.3), 4 (6.6), 5 (11))
Key data | Thermal classes | 90/110/150 °C (4A EPR/CSP · 4D EVA · 4C Silicone/glass)
Key data | Conductor range | 1.5–630 mm² (1C Class 5 tinned copper)
Key data | Bending radius | 6 × OD (min. fixed & festoon loop routing)
Key data | Low temperature | −40 to −60 °C (−40 °C Type 4A/4D · −60 °C Type 4C)
Key data | Configurations | 20 (Cat. 2 (1 kV) to Cat. 5 (11 kV))
Electrical | Voltage categories (U0/U) | 0.6/1, 1.9/3.3, 3.8/6.6 & 6.35/11 kV
Electrical | AC test voltage (5 min) | 3 / 10 / 16 / 24 kV AC (Cat. 2 / 3 / 4 / 5)
Electrical | Conductor DC resistance | BS EN 60228 / IEC 60228 Class 5 tinned
Electrical | Current rating basis | BS 7671 / ERA 69-30 (free air at 30 °C)
Thermal | Continuous temp. (Type 4A) | −40 to +90 °C (EPR / CSP)
Thermal | Continuous temp. (Type 4D) | −40 to +110 °C (EVA / EPR)
Thermal | Continuous temp. (Type 4C) | −60 to +150 °C (+180 °C peak, Silicone/Glass)
Thermal | Short-circuit temperature (5 s) | +250 °C (4A/4D) · +350 °C (4C)
Mechanical | Min. bending radius | 6 × OD (fixed & festoon loops)
Mechanical | Conductor flexibility | Class 5 flexible tinned copper
Mechanical | Max. pulling tension | 15 N/mm² of copper cross-section
Resistance | Oil & varnish resistance | EN 60811-404 & impregnating varnish resistant
Resistance | Flame retardance | BS EN / IEC 60332-1-2
Resistance | Halogen & smoke (Type 4C/4D) | Halogen-free EVA (4D) & silicone/glass (4C)
Standards | Construction standard | BS 6195 (Types 4A, 4C & 4D)
Standards | Conductor standard | BS EN 60228 / IEC 60228 Class 5
Standards | Insulation & sheath compounds | BS 7655 GP4/EI2/GP6 & HOFR/EVA
Identification | Outer surface colour | Black (4A/4D) · Red-brown/white (4C)
Identification | Voltage category coding | Cat. 2 (1 kV), 3 (3.3), 4 (6.6), 5 (11 kV)
Identification | Customs tariff (HS) | 8544.49 (≤ 1 kV) / 8544.60 (> 1 kV)

## Construction
BS 6195 Type 4A / 4C / 4D Flexible Coil-Lead and Festoon Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6195-type-4a-4c-4d-flexible-coil-lead-and-festoon-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6195. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible tinned copper conductor | Electrolytic tinned annealed copper, finely stranded Class 5 | BS EN 60228 / IEC 60228 Class 5 (1.5 to 630 mm²)
2 | Conductor separator tape | Non-hygroscopic polyester or semi-conducting tape (on HV categories ≥ 3.3 kV)
3 | Primary elastomeric insulation | Type 4A: EPR (GP4) · Type 4C: Silicone rubber (EI2) · Type 4D: EVA / high-temp EPR
4 | Composite outer sheath / glass braid | Type 4A: CSP/HOFR elastomer (90 °C) · Type 4D: EVA elastomer (110 °C) · Type 4C: heat-resistant glass-fibre braid + varnish (150 °C)
| BS 6195 Type 4A (90 °C) | EPR insulation + CSP (chlorosulphonated polyethylene / HOFR) composite sheath · −40 to +90 °C continuous
| BS 6195 Type 4D (110 °C) | High-temperature EPR/EVA insulation and sheath for Class B/F varnish baking · −40 to +110 °C continuous
| BS 6195 Type 4C (150 °C) | Silicone rubber insulation with heat-resistant lacquered glass-fibre braid · −60 to +150 °C (up to +180 °C peak)

## Series
BS 6195 Type 4A / 4C / 4D Flexible Coil-Lead and Festoon Cable – Series
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6195-type-4a-4c-4d-flexible-coil-lead-and-festoon-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6195. Values for your order are confirmed in the quotation.
Code | Series | Rating | Standard / class | Sizes | Typical use
Cat. 2 · 0.6/1 kV | Category 2 · 600/1000 V | 600/1000 V | Types 4A / 4C / 4D | 7 | LV motors, transformers & festoon loops
Cat. 3 · 1.9/3.3 kV | Category 3 · 1900/3300 V | 1.9/3.3 kV | Types 4A / 4C / 4D | 5 | 3.3 kV rotating machines & switchgear
Cat. 4 · 3.8/6.6 kV | Category 4 · 3800/6600 V | 3.8/6.6 kV | Types 4A / 4C / 4D | 4 | 6.6 kV motors, generators & unit transformers
Cat. 5 · 6.35/11 kV | Category 5 · 6350/11000 V | 6.35/11 kV | Types 4A / 4C / 4D | 4 | 11 kV winders, alternators & traction transformers

## Quality and supply
BS 6195 Type 4A / 4C / 4D Flexible Coil-Lead and Festoon Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6195-type-4a-4c-4d-flexible-coil-lead-and-festoon-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6195. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage water immersion test — 3 kV (Cat.2), 10 kV (Cat.3), 16 kV (Cat.4), 24 kV (Cat.5) for 5 min | Every manufactured length
Routine test | Conductor DC resistance — BS EN 60228 / IEC 60228 Class 5 tinned copper | Every length
Sample test | Coil varnish & baking compatibility test — Thermal ageing and solvent resistance per BS 6195 / BS 7655 | Per compound batch
Sample test | Oil immersion & vertical flame propagation — EN 60811-404 · BS EN / IEC 60332-1-2 | Per batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BS 6195 TYPE 4A CAT 3 1900/3300 V 1x70 mm² · [year] · [metre mark]
Supply | Delivery form: Non-returnable export timber drums or coils, cut-to-length
Supply | Packaging: ISPM-15 heat-treated timber drums with sealed moisture-proof ends
Supply | Minimum order: None
Supply | Lead time: None