## Request a quote
Request a quotation for BS 6708 Type 201 / 211
Application engineer · BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-201-211-armoured-trailing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type 201 & Type 211 Screened Armoured Trailing Cable – Dimensions, weights & current (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-201-211-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Type · nominal CSA mm² | Earth core CSA | Insul.+tape Ø mm | Screen Ø mm | Inner sh. Ø mm | Min. OD mm | Max. OD mm | Min. R mm | Max. pull kgf | Mass ≈ kg/km | Current (25 °C) A | Series
| Type 201 · 3×10 | — (3P only) | 7.7 | 9.7 | 25.5–27.5 | 37.3 | 39.8 | 400 | 180 | 2900 | 63 | BS 6708 Type 201 · 640/1,100 V (3 Screened Phase Cores + Pliable Wire Armour)
| Type 201 · 3×16 | — (3P only) | 9.15 | 11.15 | 28.7–30.7 | 40.6 | 43.4 | 440 | 290 | 3400 | 85 | BS 6708 Type 201 · 640/1,100 V (3 Screened Phase Cores + Pliable Wire Armour)
| Type 201 · 3×25 | — (3P only) | 10.65 | 12.65 | 32.2–34.2 | 44.6 | 47.4 | 480 | 450 | 4100 | 110 | BS 6708 Type 201 · 640/1,100 V (3 Screened Phase Cores + Pliable Wire Armour)
| Type 201 · 3×35 | — (3P only) | 11.9 | 13.9 | 35.2–37.2 | 48.3 | 51.1 | 510 | 630 | 4800 | 135 | BS 6708 Type 201 · 640/1,100 V (3 Screened Phase Cores + Pliable Wire Armour)
| Type 201 · 3×50 | — (3P only) | 13.9 | 15.9 | 39.5–41.5 | 53.6 | 57.4 | 580 | 900 | 5900 | 170 | BS 6708 Type 201 · 640/1,100 V (3 Screened Phase Cores + Pliable Wire Armour)
| Type 201 · 3×70 | — (3P only) | 16 | 18 | 44.5–47.0 | 60.7 | 64.5 | 650 | 1260 | 7700 | 205 | BS 6708 Type 201 · 640/1,100 V (3 Screened Phase Cores + Pliable Wire Armour)
| Type 201 · 3×95 | — (3P only) | 17.55 | 19.55 | 52.5–55.5 | 71.8 | 75.8 | 760 | 1710 | 10900 | 250 | BS 6708 Type 201 · 640/1,100 V (3 Screened Phase Cores + Pliable Wire Armour)
| Type 201 · 3×120 | — (3P only) | 20.35 | 22.35 | 56.6–59.6 | 76.7 | 81 | 810 | 2000 | 12500 | 295 | BS 6708 Type 201 · 640/1,100 V (3 Screened Phase Cores + Pliable Wire Armour)
| Type 211 · 3×10+10E | 1×10 mm² | 7.7 | 9.7 | 27.9–29.9 | 39.8 | 42.3 | 430 | 240 | 3200 | 63 | BS 6708 Type 211 · 640/1,100 V (3 Screened Phase Cores + 1 Unscreened Earth Core + Pliable Wire Armour)
| Type 211 · 3×16+16E | 1×16 mm² | 9.15 | 11.15 | 31.6–33.6 | 44 | 46.8 | 470 | 380 | 3900 | 85 | BS 6708 Type 211 · 640/1,100 V (3 Screened Phase Cores + 1 Unscreened Earth Core + Pliable Wire Armour)
| Type 211 · 3×25+16E | 1×16 mm² | 10.65 | 12.65 | 35.4–37.4 | 48.5 | 51.3 | 520 | 540 | 4700 | 110 | BS 6708 Type 211 · 640/1,100 V (3 Screened Phase Cores + 1 Unscreened Earth Core + Pliable Wire Armour)
| Type 211 · 3×35+25E | 1×25 mm² | 11.9 | 13.9 | 38.8–40.8 | 52.7 | 56.5 | 570 | 780 | 5600 | 135 | BS 6708 Type 211 · 640/1,100 V (3 Screened Phase Cores + 1 Unscreened Earth Core + Pliable Wire Armour)
| Type 211 · 3×50+35E | 1×35 mm² | 13.9 | 15.9 | 43.7–46.2 | 59.7 | 63.5 | 640 | 1110 | 7300 | 170 | BS 6708 Type 211 · 640/1,100 V (3 Screened Phase Cores + 1 Unscreened Earth Core + Pliable Wire Armour)
| Type 211 · 3×70+50E | 1×50 mm² | 16 | 18 | 51.8–54.8 | 68.8 | 72.8 | 730 | 1560 | 9500 | 205 | BS 6708 Type 211 · 640/1,100 V (3 Screened Phase Cores + 1 Unscreened Earth Core + Pliable Wire Armour)
| Type 211 · 3×95+70E | 1×70 mm² | 17.55 | 19.55 | 60.3–63.3 | 80.6 | 84.9 | 850 | 2000 | 13300 | 250 | BS 6708 Type 211 · 640/1,100 V (3 Screened Phase Cores + 1 Unscreened Earth Core + Pliable Wire Armour)
| Type 211 · 3×120+70E | 1×70 mm² | 20.35 | 22.35 | 64.9–67.9 | 86.2 | 90.5 | 910 | 2000 | 15400 | 295 | BS 6708 Type 211 · 640/1,100 V (3 Screened Phase Cores + 1 Unscreened Earth Core + Pliable Wire Armour)
Minimum bending radius is 10 × maximum overall diameter across all 16 configurations (400 to 810 mm on Type 201; 430 to 910 mm on Type 211).

## Electrical & impedance data
BS 6708 Type 201 & Type 211 Screened Armoured Trailing Cable – Electrical & impedance data (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-201-211-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998. Values for your order are confirmed in the quotation.
Type · nominal CSA mm² | Max. phase DC res. Ω/km | Max. earth DC res. Ω/km | 3-screen parallel res. Ω/km | Max. armour DC res. Ω/km | Reactance (50 Hz) Ω/km | Reactance (60 Hz) Ω/km | Min. IR (20 °C) MΩ·km | 3-phase V-drop mV/A/m | Series
Type 201 · 3×10 | 1.95 | — | 1.33 | 1.97 | 0.121 | 0.145 | 560 | 4.11 | BS 6708 Type 201 · Electrical Parameters
Type 201 · 3×16 | 1.24 | — | 1.61 | 1.76 | 0.111 | 0.134 | 435 | 2.62 | BS 6708 Type 201 · Electrical Parameters
Type 201 · 3×25 | 0.795 | — | 1.1 | 1.45 | 0.107 | 0.128 | 375 | 1.68 | BS 6708 Type 201 · Electrical Parameters
Type 201 · 3×35 | 0.565 | — | 1.2 | 1.03 | 0.102 | 0.123 | 325 | 1.2 | BS 6708 Type 201 · Electrical Parameters
Type 201 · 3×50 | 0.393 | — | 1.4 | 0.715 | 0.099 | 0.119 | 285 | 0.85 | BS 6708 Type 201 · Electrical Parameters
Type 201 · 3×70 | 0.277 | — | 0.7 | 0.504 | 0.097 | 0.116 | 260 | 0.61 | BS 6708 Type 201 · Electrical Parameters
Type 201 · 3×95 | 0.21 | — | 0.85 | 0.382 | 0.096 | 0.116 | 250 | 0.47 | BS 6708 Type 201 · Electrical Parameters
Type 201 · 3×120 | 0.164 | — | 0.5 | 0.299 | 0.095 | 0.114 | 250 | 0.38 | BS 6708 Type 201 · Electrical Parameters
Type 211 · 3×10+10E | 1.95 | 1.950 | 1.33 | 1.81 | 0.121 | 0.145 | 560 | 4.11 | BS 6708 Type 211 · Electrical Parameters
Type 211 · 3×16+16E | 1.24 | 1.240 | 1.61 | 1.63 | 0.111 | 0.134 | 435 | 2.62 | BS 6708 Type 211 · Electrical Parameters
Type 211 · 3×25+16E | 0.795 | 1.240 | 1.1 | 1.45 | 0.107 | 0.128 | 375 | 1.68 | BS 6708 Type 211 · Electrical Parameters
Type 211 · 3×35+25E | 0.565 | 0.795 | 1.2 | 1.03 | 0.102 | 0.123 | 325 | 1.2 | BS 6708 Type 211 · Electrical Parameters
Type 211 · 3×50+35E | 0.393 | 0.565 | 1.4 | 0.715 | 0.099 | 0.119 | 285 | 0.85 | BS 6708 Type 211 · Electrical Parameters
Type 211 · 3×70+50E | 0.277 | 0.393 | 0.7 | 0.504 | 0.097 | 0.116 | 260 | 0.61 | BS 6708 Type 211 · Electrical Parameters
Type 211 · 3×95+70E | 0.21 | 0.277 | 0.85 | 0.382 | 0.096 | 0.116 | 250 | 0.47 | BS 6708 Type 211 · Electrical Parameters
Type 211 · 3×120+70E | 0.164 | 0.277 | 0.5 | 0.299 | 0.095 | 0.114 | 250 | 0.38 | BS 6708 Type 211 · Electrical Parameters
In Type 211, the unscreened Green/Yellow earth conductor operates in parallel with the three composite phase screens and the galvanized steel pliable wire armour.

## Technical data
BS 6708 Type 201 & Type 211 Screened Armoured Trailing Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-201-211-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 640/1,100 V (2.5 kV AC / 5 min test)
Key data | Core layout | 3P / 3P+E + PWA (Type 201 (3P) · Type 211 (3P+E))
Key data | Phase CSA range | 10–120 mm² (16 sizes · 63–295 A at 25 °C)
Key data | Max. conductor T | +90 °C (MEPR insulation (250 °C SC))
Key data | Min. operating T | −25 °C (Yellow-striped black PCP)
Key data | Min. bend radius | 10 × OD (400–910 mm across 10–120 mm²)
Electrical | Rated voltage (U0/U) | 640/1,100 V AC (U0/U)
Electrical | AC test voltage | 2.5 kV AC for 5 minutes on finished cable
Electrical | Current ratings (25 °C) | 63 to 295 A continuous current rating at 25 °C ambient across 10 to 120 mm²
Electrical | Screens, earth & armour DC res. | Individual composite copper/nylon braid over 3 phase cores (0.500–1.610 Ω/km in parallel) + galvanized steel pliable wire armour (0.299–1.970 Ω/km) + unscreened earth core (10–70 mm²) in Type 211
Electrical | Reactance, IR & voltage drop | 0.095–0.121 Ω/km (50 Hz) / 0.114–0.145 Ω/km (60 Hz) reactance · 250–560 MΩ·km min. IR at 20 °C · 0.38–4.11 mV/A/m 3-phase voltage drop
Thermal | Max. conductor & SC temperature | +90 °C maximum continuous conductor temperature · +250 °C short-circuit temperature (MEPR insulation)
Thermal | Operating temperature range | −25 °C to +90 °C operating range (current ratings referenced at 25 °C ambient)
Mechanical | Minimum bending radius | 400 to 810 mm (Type 201) · 430 to 910 mm (Type 211), corresponding to 10 × overall diameter
Mechanical | Maximum pulling tension | 180 to 2,000 kgf (Type 201) · 240 to 2,000 kgf (Type 211) maximum pulling tension
Mechanical | Multi-layer armoured construction | MEPR-insulated Class 5 tinned copper cores + composite Cu/nylon phase screens + elastomeric cradle + PCP inner bedding + galvanized steel PWA + heavy-duty PCP outer jacket
Resistance | Flame retardance | Flame retardant polychloroprene inner and outer sheaths to BS 6708:1998 / IEC 60332-1-2
Resistance | Crush, oil & quarry resistance | Pliable galvanized steel wire armour + heavy-duty PCP jacket resists rockfall impact, quarry abrasion, mineral oils (IEC 60811-404) and mine water
Standards | Standards compliance | BS 6708:1998 (Types 201 & 211); BS EN / IEC 60228 Class 5; BS 7655
Standards | Designated duty | Mobile and semi-mobile mining/quarrying plant, roadway power extensions, mobile crushers, conveyors and face equipment
Identification | Core identification colours | Power cores: Red, Yellow, Brown textile identification tape under composite screen · Earth core (Type 211): Green/Yellow
Identification | Outer sheath & stripe | Heavy-duty black polychloroprene (PCP) outer jacket with longitudinal yellow identification stripe

## Construction
BS 6708 Type 201 & Type 211 Screened Armoured Trailing Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-201-211-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase & earth conductors | Flexible stranded tinned annealed copper wire, BS EN / IEC 60228 Class 5 (10 to 120 mm² phase; 10 to 70 mm² earth in Type 211) | IEC 60228 Class 5
2 | Core insulation | Mining-grade ethylene propylene rubber (MEPR) on all phase and earth conductors (Ø 7.70 to 20.35 mm over phase insulation+tape) | BS 7655 MEPR
3 | Identification tape | Coloured textile tape over MEPR insulation (Red, Yellow, Brown on phase cores; Green/Yellow on Type 211 earth core)
4 | Composite phase screens | Tinned copper wire and nylon braided composite screen over each of the 3 phase cores (Ø 9.70 to 22.35 mm; 0.500–1.610 Ω/km in parallel)
5 | Elastomeric cradle | Central elastomeric cradle filler around which the cores are laid up
6 | Inner bedding sheath | Extruded polychloroprene (PCP) inner sheath (Ø 25.5 to 67.9 mm)
7 | Pliable wire armour (PWA) | Pliable stranded galvanized steel wire armour (0.299 to 1.970 Ω/km DC resistance at 20 °C) | BS 6708:1998 PWA
8 | Outer jacket | Heavy-duty flame-retardant black polychloroprene (PCP) outer jacket with longitudinal yellow identification stripe | BS 6708:1998 / BS 7655 EM2
| BS 6708 Type 201 · 3×10 to 3×120 mm² | 3 composite-screened MEPR phase cores (Red, Yellow, Brown) around elastomeric cradle + PCP inner sheath + galvanized steel PWA + yellow-striped black PCP jacket
| BS 6708 Type 211 · 3×10+10E to 3×120+70E mm² | 3 composite-screened MEPR phase cores + 1 unscreened Green/Yellow earth core (10–70 mm²) + PCP inner sheath + galvanized steel PWA + yellow-striped black PCP jacket

## Quality and supply
BS 6708 Type 201 & Type 211 Screened Armoured Trailing Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-201-211-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage dielectric test — 2.5 kV AC for 5 minutes applied on finished cable | Every drum
Routine test | Phase, earth, composite screen & armour DC resistance — Verified at 20 °C against BS 6708:1998 limits (0.164–1.950 Ω/km phase; 0.500–1.610 Ω/km screens; 0.299–1.970 Ω/km armour) | Every drum
Sample test | Insulation resistance verification — 250 to 560 MΩ·km minimum insulation resistance at 20 °C | Every drum
Sample test | Flame retardance & oil resistance — IEC 60332-1-2 vertical flame test and IEC 60811-404 oil immersion on heavy-duty PCP sheath | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · BS 6708:1998 TYPE 201 (or TYPE 211) · 640/1100 V · [size] · PCP (with longitudinal yellow stripe)
Supply | Delivery form: Heat-treated seaworthy wooden drums lagged with solid timber battens
Supply | Lengths: Custom cut-to-length reels per roadway/quarry feeder schedule
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None