## Request a quote
Request a quotation for BS 6708 Type 321 & Type 331 (1.9/3.3 kV)
Application engineer · BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-321-331-armoured-trailing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type 321 & 331 Armoured Trailing Cable (1.9/3.3 kV) – Dimensions & mechanical (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-321-331-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation BS 6708 Type | Phase mm² | Earth mm² | Phase insul. Ø mm | Phase screen Ø mm | Earth insul. Ø mm | Inner min Ø mm | Inner max Ø mm | Min. OD mm | Max. OD mm | Min. bend mm | Max. pull kgf | Mass ≈ kg/km
| Type 331 · 3×25 + 16E (Scr) | 25 | 16 | 13.5 | 15.50 | 15.5 | 42.2 | 44.7 | 57.8 | 61.6 | 620 | 540 | 6400
| Type 331 · 3×35 + 25E (Scr) | 35 | 25 | 15.1 | 17.10 | 17.1 | 48.2 | 50.7 | 64.6 | 68.4 | 690 | 780 | 7800
| Type 331 · 3×50 + 35E (Scr) | 50 | 35 | 16.2 | 18.20 | 18.2 | 52.6 | 55.6 | 69.8 | 73.8 | 740 | 1110 | 9100
| Type 331 · 3×70 + 50E (Scr) | 70 | 50 | 18.15 | 20.15 | 20.15 | 60 | 63 | 80.3 | 84.6 | 850 | 1560 | 12400
| Type 331 · 3×95 + 70E (Scr) | 95 | 70 | 19.6 | 21.60 | 21.6 | 65.1 | 68.9 | 86.4 | 90.7 | 910 | 2000 | 14600
| Type 331 · 3×120 + 70E (Scr) | 120 | 70 | 21.95 | 23.95 | 23.95 | 68.8 | 72.6 | 90.9 | 95.2 | 960 | 2000 | 16300
| Type 331 · 3×150 + 70E (Scr) | 150 | 70 | 23.1 | 25.40 | 25.4 | 71.5 | 74 | 93.8 | 98.1 | 980 | 2000 | 18200
| Type 321 · 3×35 + 35E (Unscr) | 35 | 35 | 15.1 | Unscreened | 15.1 | 44.3 | 46.8 | 60.3 | 64.1 | 640 | 840 | 4900
| Type 321 · 3×50 + 50E (Unscr) | 50 | 50 | 16.2 | Unscreened | 16.2 | 51.3 | 54.3 | 68.3 | 72.3 | 720 | 1200 | 6400
| Type 321 · 3×70 + 70E (Unscr) | 70 | 70 | 18.15 | Unscreened | 18.15 | 56.4 | 59.4 | 74.4 | 78.4 | 790 | 1680 | 7700
| Type 321 · 3×95 + 95E (Unscr) | 95 | 95 | 19.6 | Unscreened | 19.6 | 63.8 | 66.8 | 84.9 | 89.2 | 890 | 2000 | 10800
| Type 321 · 3×120 + 120E (Unscr) | 120 | 120 | 21.95 | Unscreened | 21.95 | 67.5 | 71.3 | 89.4 | 93.7 | 940 | 2000 | 12300
In Type 331, the unscreened earth core insulation is built up to match the diameter over the screened phase cores (15.50–25.40 mm) so all four cores form a symmetrical assembly.
In Type 321, all four unscreened cores (3 phase + 1 earth) have identical copper cross-sections and insulated diameters (15.10–21.95 mm).

## Electrical parameters
BS 6708 Type 321 & 331 Armoured Trailing Cable (1.9/3.3 kV) – Electrical parameters (25 °C) (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-321-331-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Designation BS 6708 Type | Cont. current A (25 °C) | Phase DC 20 °C Ω/km | Earth DC 20 °C Ω/km | 3 screens par. Ω/km | Armour DC 20 °C Ω/km | Reactance 50 Hz Ω/km | Reactance 60 Hz Ω/km | Min. IR 20 °C MΩ·km | 3-ph V-drop mV/A/m
Type 331 · 3×25 + 16E (Scr) | 110 | 0.795 | 1.24 | 1.350 | 0.965 | 0.125 | 0.15 | 1250 | 1.69
Type 331 · 3×35 + 25E (Scr) | 135 | 0.565 | 0.795 | 0.800 | 0.844 | 0.117 | 0.14 | 1100 | 1.21
Type 331 · 3×50 + 35E (Scr) | 170 | 0.393 | 0.565 | 0.700 | 0.715 | 0.113 | 0.136 | 950 | 0.85
Type 331 · 3×70 + 50E (Scr) | 205 | 0.277 | 0.393 | 0.690 | 0.488 | 0.108 | 0.129 | 820 | 0.61
Type 331 · 3×95 + 70E (Scr) | 250 | 0.21 | 0.277 | 0.840 | 0.382 | 0.105 | 0.126 | 720 | 0.48
Type 331 · 3×120 + 70E (Scr) | 295 | 0.164 | 0.277 | 0.550 | 0.299 | 0.101 | 0.121 | 660 | 0.39
Type 331 · 3×150 + 70E (Scr) | 320 | 0.132 | 0.277 | 0.550 | 0.24 | 0.098 | 0.118 | 600 | 0.32
Type 321 · 3×35 + 35E (Unscr) | 135 | 0.565 | 0.565 | — | 0.99 | 0.117 | 0.14 | 1100 | 1.21
Type 321 · 3×50 + 50E (Unscr) | 170 | 0.393 | 0.393 | — | 0.76 | 0.113 | 0.136 | 950 | 0.85
Type 321 · 3×70 + 70E (Unscr) | 205 | 0.277 | 0.277 | — | 0.53 | 0.108 | 0.129 | 820 | 0.61
Type 321 · 3×95 + 95E (Unscr) | 250 | 0.21 | 0.21 | — | 0.4 | 0.105 | 0.126 | 720 | 0.48
Type 321 · 3×120 + 120E (Unscr) | 295 | 0.164 | 0.164 | — | 0.32 | 0.101 | 0.121 | 660 | 0.39
Armour DC resistance at 20 °C (0.240–0.990 Ω/km) works in parallel with the insulated earth core (and the 3 phase screens on Type 331) to provide high earth-fault conductivity.

## Technical data
BS 6708 Type 321 & 331 Armoured Trailing Cable (1.9/3.3 kV) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-321-331-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1,900/3,300 V (6.5 kV AC routine test)
Key data | Core arrangement | 3P + 1E + PWA (331 (scr) · 321 (unscr))
Key data | Phase size range | 25–150 mm² (12 standard sizes)
Key data | Ampacity (25 °C) | 110–320 A (Continuous ambient rating)
Key data | Operating temp. | −25 to +85 °C (MEPR / twin PCP)
Key data | Min. bend radius | 10 × OD (620+) (Pliable wire armoured)
Electrical | Rated voltage U0/U | 1,900/3,300 V AC · 6.5 kV routine AC test voltage
Electrical | Current rating (25 °C) | 110 to 320 A continuous at 25 °C ambient (Type 331) · 135 to 295 A (Type 321)
Electrical | Core screening & earth path | Type 331: Composite Cu/nylon braid on 3 phase cores (0.55–1.35 Ω/km parallel) + insulated earth + pliable GSW armour · Type 321: Unscreened cores + full-size earth + pliable GSW armour
Thermal | Ambient temperature range | −25 °C to +85 °C
Thermal | Max. conductor temperature | +90 °C continuous MEPR operating temperature
Mechanical | Min. bending radius | 620–980 mm (Type 331) · 640–940 mm (Type 321) (~10 × max OD)
Mechanical | Max. pulling tension | 540 to 2,000 kgf (Type 331) · 840 to 2,000 kgf (Type 321)
Mechanical | Armour & sheaths | Extruded PCP inner bedding sheath + pliable galvanised steel wire armour (PWA) + heavy-duty black PCP outer sheath with blue stripe
Resistance | Crush & impact protection | Pliable galvanised steel wire armour over PCP inner sheath resists rockfall and quarry vehicle run-over
Resistance | Flame, oil & water | Heavy-duty flame-retardant polychloroprene (PCP) outer sheath resists oil, mine water and abrasion
Standards | Construction standard | BS 6708:1998 (Flexible cables for use at mines and quarries)
Standards | Conductor & insulation | IEC 60228 Class 5 tinned annealed copper · mining-grade EPR (MEPR) insulation
Standards | Routine electrical test | 6.5 kV AC routine dielectric test · min. 600–1,250 MΩ·km insulation resistance at 20 °C
Identification | Phase core identification | Red, Yellow and Brown phase cores + insulated earth core
Identification | Outer sheath marking | Black heavy-duty PCP outer sheath with longitudinal blue identification stripe

## Construction
BS 6708 Type 321 & 331 Armoured Trailing Cable (1.9/3.3 kV) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-321-331-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible phase & earth conductors (4) | Flexible stranded tinned annealed copper wire (IEC 60228 Class 5, 25 to 150 mm²) | IEC 60228 Class 5
2 | MEPR core insulation | Mining-grade ethylene propylene rubber (MEPR) on all 3 phase cores (Red, Yellow, Brown) and earth core | BS 6708:1998 (6.5 kV test)
3 | Composite copper / nylon phase screen (Type 331) | Tinned copper wire and nylon braided screen over each of the 3 phase cores (omitted on Type 321 and earth core) | Type 331 phase screen
4 | Elastomeric centre | Shaped central elastomeric filler maintaining 4-core geometry under impact | BS 6708:1998
5 | Extruded PCP inner bedding sheath | Polychloroprene (PCP) elastomeric inner sheath (42.2 to 74.0 mm diameter) | BS 6708:1998
6 | Pliable galvanised steel wire armour | Stranded galvanised steel pliable wire armour (PWA, 0.240 to 0.990 Ω/km at 20 °C) | BS 6708:1998
7 | Heavy-duty PCP outer sheath | Heavy-duty flame-retardant polychloroprene (PCP) compound, black with longitudinal blue identification stripe | BS 6708:1998
| BS 6708 Type 331 (25–150 mm² · Screened) | 3 copper/nylon braided-screened MEPR phase cores + 1 unscreened MEPR earth core (16–70 mm²) + pliable GSW armour
| BS 6708 Type 321 (35–120 mm² · Unscreened) | 3 unscreened MEPR phase cores + 1 equal-CSA unscreened MEPR earth core (35–120 mm²) + pliable GSW armour

## Quality and supply
BS 6708 Type 321 & 331 Armoured Trailing Cable (1.9/3.3 kV) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-321-331-armoured-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708:1998 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 6.5 kV AC dielectric withstand test — 6.5 kV AC routine voltage test on 1,900/3,300 V MEPR-insulated cores per BS 6708:1998 | Every shipping drum
Routine test | Phase, earth, screen & armour DC resistance — Verified on all phase conductors, earth core, 3 parallel screens (Type 331) and pliable steel wire armour per BS 6708:1998 | Every shipping drum
Sample test | PCP sheath flame, oil & mechanical testing — Heavy-duty flame-retardant black PCP outer sheath with blue stripe tested to BS 6708:1998 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · BS 6708:1998 · TYPE 321 / TYPE 331 · 1900/3300V (BLUE STRIPE)
Supply | Delivery form: Export seaworthy fumigated wooden drums matched to 10 × OD bend radius
Supply | Lengths: Standard drum lengths or custom cut lengths with gland termination allowance
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None