## Request a quote
Request a quotation for BS 6708 Type 44 Drill Cable
Application engineer · BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-44-drilling-machine-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type 44 Handheld Drilling Machine Cable – Dimensions & electrical data (1)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-44-drilling-machine-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Type · nominal CSA mm² | Conductor stranding | Cond. Ø mm | EPR insul. mm | Total screen mm² | Outer PCP sh. mm | Min. OD mm | Max. OD mm | Min. R mm | Max. pull kgf | Mass ≈ kg/km | Cu wt kg/km | Current (25 °C) A | 1 s SC A | Core DC res. Ω/km | 3-scr. res. Ω/km
| Type 44 · 5×6 (3×6 scr. + 1×6E + 1×6P) | 84/0.30 | 3.3 | 1 | 11 | 3 | 24.7 | 26.7 | 241 | 218 | 1150 | 400 | 46 | 908 | 3.48 | 11
Three composite tinned-copper/nylon phase screens provide 11 mm² total metallic screen area (≤ 11.0 Ω/km in parallel at 20 °C), increasing copper mass to 400 kg/km vs 150 kg/km on Type 43.

## Technical data
BS 6708 Type 44 Handheld Drilling Machine Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-44-drilling-machine-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 72/125 V (1.5 kV AC core test voltage)
Key data | Core layout | 5 × 6 mm² (3 scr. phase + 1E + 1 pilot)
Key data | Overall Ø | 24.7–26.7 mm (1,150 kg/km · 46 A at 25 °C)
Key data | Max. conductor T | +90 °C (EPR insulation (+85 °C sheath))
Key data | Min. operating T | −25 °C (Heavy-duty chloroprene (PCP))
Key data | Min. bend radius | 9 × OD (241 mm · 218 kgf max pull)
Electrical | Rated voltage (U0/U) | 72/125 V AC (U0/U, written 125/72 V on UK drill gate-end transformers)
Electrical | AC test voltage | 1.5 kV AC dielectric test on all cores
Electrical | Current & short-circuit rating | 46 A continuous current rating at 25 °C ambient · 908 A 1-second short-circuit rating
Electrical | Max. core & screen DC resistance | 3.48 Ω/km max. DC resistance at 20 °C on phase, earth and pilot cores · 11.0 Ω/km max. across 3 phase screens in parallel
Electrical | Phase core screening | Individual composite tinned copper and nylon braided screen over each of the 3 phase cores (11 mm² total screen CSA); earth and pilot cores unscreened
Thermal | Max. conductor temperature | +90 °C maximum continuous conductor temperature (EPR insulation)
Thermal | Operating temperature range | −25 °C to +85 °C ambient flex / coalface service range (current rating referenced at 25 °C)
Mechanical | Minimum bending radius | 241 mm minimum bending radius (9 × maximum overall diameter)
Mechanical | Max. pulling tension & weight | 218 kgf maximum pulling tension · 1,150 kg/km total mass (400 kg/km copper weight)
Mechanical | Dimensional profile | 5 × 6 mm² (84/0.30 mm, Ø 3.30 mm) · 1.00 mm EPR insulation · elastomeric cradle · rubber bedding · 3.0 mm heavy-duty PCP outer sheath · 24.7–26.7 mm OD
Resistance | Flame retardance | Flame retardant polychloroprene outer sheath to BS 6708 / BS EN 60332-1-2
Resistance | Coalface mechanical & chemical resistance | 3.0 mm heavy-duty PCP sheath + nylon-reinforced copper phase screens resist coalface abrasion, oil, water and repetitive flexing
Standards | Standards compliance | BS 6708 Type 44; IEC 60228 Class 5; BS 7655
Standards | Designated duty | 125 V 3-phase handheld rotary coal and rock drilling machines requiring metallic phase screens
Identification | Core identification | Coloured textile identification tape over EPR insulation (3 composite-screened phase cores + 1 unscreened earth + 1 unscreened pilot)
Identification | Outer sheath | Heavy-duty black chloroprene (PCP) outer sheath (3.0 mm radial thickness)

## Construction
BS 6708 Type 44 Handheld Drilling Machine Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-44-drilling-machine-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 5 × 6 mm² conductors | Electrolytic stranded tinned copper wire, IEC 60228 Class 5 (84/0.30 mm, Ø 3.30 mm on all 5 cores) | IEC 60228 Class 5
2 | Core insulation | EPR (ethylene-propylene rubber), 1.00 mm nominal radial thickness | BS 7655 / BS 6708
3 | Identification tape | Coloured textile tape over EPR insulation for phase, earth and pilot core identification
4 | Composite phase screens | Tinned copper and nylon braided screen over the 3 phase cores (11 mm² total screen CSA; ≤ 11 Ω/km in parallel); pilot and earth cores unscreened
5 | Elastomeric cradle | Central elastomeric cradle around which the five cores are laid up in contact
6 | Inner bedding | Rubber-based elastomeric bedding compound extruded over laid-up cores
7 | Outer sheath | Heavy-duty flame-retardant polychloroprene (chloroprene / PCP) outer sheath, black (3.0 mm radial wall) | BS 6708 / BS 7655 EM2
| BS 6708 Type 44 · 5×6 mm² | 3 composite-screened phase cores (11 mm² total screen) + 1 unscreened earth + 1 unscreened pilot around elastomeric cradle + 3.0 mm PCP jacket

## Quality and supply
BS 6708 Type 44 Handheld Drilling Machine Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-44-drilling-machine-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage dielectric test — 1.5 kV AC applied on all 5 × 6 mm² insulated cores | Every drum
Routine test | Core & composite screen DC resistance check — ≤ 3.48 Ω/km on phase/earth/pilot cores; ≤ 11.0 Ω/km across 3 phase screens in parallel at 20 °C | Every drum
Sample test | Flame retardance test — Self-extinguishing heavy-duty chloroprene outer sheath per BS 6708 / BS EN 60332-1-2 | Production batch
Sample test | Dimensional & sheath wall inspection — Verification of 3.0 mm radial outer PCP wall and 24.7–26.7 mm overall diameter limits | Every drum
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · BS 6708 TYPE 44 · 125/72 V · 5x6 mm² · PCP
Supply | Delivery form: Heat-treated seaworthy wooden drums lagged with solid timber battens
Supply | Lengths: Custom cut-to-length reels per coalface drill schedule
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None