## Request a quote
Request a quotation for BS 6708 Type 506 / 512 / 518 / 524 (320/550 V)
Application engineer · BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-506-512-518-524-control-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type 506, 512, 518 & 524 Control Cable (320/550 V) – Dimensions & mechanical (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-506-512-518-524-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation BS 6708 Type | Cores No. | Core CSA mm² | Stranding n/mm | Cond. Ø mm | Insul. mm | Inner wall mm | Inner min Ø mm | Inner max Ø mm | Armour n/mm | Outer wall mm | Min. OD mm | Max. OD mm | Min. bend mm | Cu mass kg/km | Mass ≈ kg/km
| Type 506 · 6 × 1.34 mm² | 6 | 1.34 | 19/0.30 | 1.6 | 0.4 | 3.5 | 14.8 | 16.8 | 7/0.45 | 1.8 | 22.1 | 23.6 | 236 | 150 | 1020
| Type 512 · 12 × 1.34 mm² | 12 | 1.34 | 19/0.30 | 1.6 | 0.4 | 1.8 | 14.8 | 16.8 | 7/0.45 | 1.8 | 22.1 | 23.6 | 236 | 300 | 1200
| Type 518 · 18 × 1.34 mm² | 18 | 1.34 | 19/0.30 | 1.6 | 0.4 | 1.5 | 16.5 | 18.5 | 7/0.45 | 1.8 | 22.8 | 25.3 | 253 | 450 | 1400
| Type 524 · 24 × 0.93 mm² | 24 | 0.93 | 19/0.25 | 1.3 | 0.4 | 1.5 | 17.9 | 19.9 | 7/0.45 | 1.8 | 24.2 | 26.7 | 267 | 450 | 1600
BS 6708 Part 5 control cable numbers encode the core count in the last two digits: Type 506 = 6×1.34 mm², Type 512 = 12×1.34 mm², Type 518 = 18×1.34 mm², Type 524 = 24×0.93 mm².
Type 506 uses a thicker 3.5 mm inner sheath so its inner sheath diameter (14.8–16.8 mm) and overall OD (22.1–23.6 mm) match Type 512, allowing shared flameproof gland hardware.

## Electrical parameters
BS 6708 Type 506, 512, 518 & 524 Control Cable (320/550 V) – Electrical parameters (25 °C) (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-506-512-518-524-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Designation BS 6708 Type | Current rating A (25 °C) | Cond. DC 20 °C Ω/km | Armour DC 20 °C Ω/km | 3 screens par. Ω/km | 1-ph / DC V-drop mV/A/m | 3-ph V-drop mV/A/m
Type 506 · 6 × 1.34 mm² | 16 | 15.4 | 5.4 | 37.3 | 34 | 30
Type 512 · 12 × 1.34 mm² | 13 | 15.4 | 5.4 | 37.3 | 34 | 30
Type 518 · 18 × 1.34 mm² | 11 | 15.4 | 4.76 | 37.3 | 34 | 30
Type 524 · 24 × 0.93 mm² | 8 | 22.1 | 4.5 | 44.7 | 50 | 43
All individual tinned-copper/nylon core screens are laid up in contact with each other inside the rubber inner sheath.

## Technical data
BS 6708 Type 506, 512, 518 & 524 Control Cable (320/550 V) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-506-512-518-524-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 320/550 V (1.5 kV AC routine test)
Key data | Core counts | 6, 12, 18 & 24C (506 · 512 · 518 · 524)
Key data | Core screening | Cu/Nylon Braid (Every core screened)
Key data | Ampacity (25 °C) | 8–16 A (Continuous control duty)
Key data | Operating temp. | −25 to +85 °C (EPR/TPE + PCP)
Key data | Min. bend radius | 10 × OD (236+) (7/0.45 mm pliable armour)
Electrical | Rated voltage U0/U | 320/550 V AC · 1.5 kV routine AC test voltage
Electrical | Current rating (25 °C) | 16 A (Type 506: 6×1.34) · 13 A (Type 512: 12×1.34) · 11 A (Type 518: 18×1.34) · 8 A (Type 524: 24×0.93)
Electrical | Conductor & screen DC resistance | Conductors: 15.4 Ω/km (1.34 mm²) / 22.1 Ω/km (0.93 mm²) · 3 screens in parallel: 37.3 Ω/km (506/512/518) / 44.7 Ω/km (524)
Electrical | Armour DC resistance (20 °C) | 5.40 Ω/km (Types 506 & 512) · 4.76 Ω/km (Type 518) · 4.50 Ω/km (Type 524)
Thermal | Ambient temperature range | −25 °C to +85 °C
Thermal | Max. conductor temperature | +90 °C continuous EPR/TPE operating temperature
Mechanical | Min. bending radius | 236 mm (Types 506 & 512) · 253 mm (Type 518) · 267 mm (Type 524) (10 × max OD)
Mechanical | Pliable armour & sheaths | Rubber inner sheath (1.5–3.5 mm) + 7/0.45 mm pliable galvanised steel wire armour + 1.8 mm heavy-duty chloroprene outer sheath
Resistance | Crush & impact protection | 7/0.45 mm pliable galvanised steel wire armour between rubber sheaths resists rockfall and crush
Resistance | Flame, oil & gas environment | Heavy-duty chloroprene (PCP) jacket for deep underground mines with explosive gases and coal dust
Standards | Construction standard | BS 6708 (Part 5 pliable-armoured multi-core control cables)
Standards | Conductor class | IEC 60228 Class 5 flexible stranded tinned copper (19/0.30 mm or 19/0.25 mm)
Standards | Routine voltage test | 1.5 kV AC routine dielectric test on all control cores
Identification | Type designation | Type 506 (6-core) · Type 512 (12-core) · Type 518 (18-core) · Type 524 (24-core)
Identification | Screen lay-up | All individual copper/nylon braided core screens laid up in mutual contact inside inner sheath

## Construction
BS 6708 Type 506, 512, 518 & 524 Control Cable (320/550 V) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-506-512-518-524-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Control conductors (6, 12, 18 or 24) | Electrolytic stranded tinned copper wire, IEC 60228 Class 5 (19/0.30 mm = 1.34 mm² or 19/0.25 mm = 0.93 mm²) | IEC 60228 Class 5
2 | Control core insulation | EPR or TPE dielectric (0.4 mm nominal radial thickness, 1.5 kV AC routine test) | BS 6708
3 | Individual composite copper / nylon screen | Tinned copper wire and nylon braided screen over every core, laid up in mutual contact (37.3 or 44.7 Ω/km for 3 screens in parallel) | BS 6708
4 | Rubber inner bedding sheath | Rubber-based inner sheath compound (3.5 mm on Type 506; 1.8 mm on Type 512; 1.5 mm on Types 518 & 524) | BS 6708
5 | Pliable galvanised steel wire armour | 7/0.45 mm galvanised steel pliable wire armour (4.50 to 5.40 Ω/km at 20 °C) | BS 6708
6 | Heavy-duty chloroprene outer sheath | Heavy-duty flame-retardant polychloroprene (chloroprene / PCP, 1.8 mm radial wall) | BS 6708
| BS 6708 Type 506 (6 × 1.34 mm²) | 6 individually screened 1.34 mm² cores · 3.5 mm inner sheath · 22.1–23.6 mm OD (shares gland size with Type 512)
| BS 6708 Type 512 (12 × 1.34 mm²) | 12 individually screened 1.34 mm² cores · 1.8 mm inner sheath · 22.1–23.6 mm OD · 13 A at 25 °C
| BS 6708 Type 518 (18 × 1.34 mm²) | 18 individually screened 1.34 mm² cores · 1.5 mm inner sheath · 22.8–25.3 mm OD · 11 A at 25 °C
| BS 6708 Type 524 (24 × 0.93 mm²) | 24 individually screened 0.93 mm² cores · 1.5 mm inner sheath · 24.2–26.7 mm OD · 8 A at 25 °C

## Quality and supply
BS 6708 Type 506, 512, 518 & 524 Control Cable (320/550 V) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-506-512-518-524-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1.5 kV AC dielectric withstand test — 1.5 kV AC routine test on all 320/550 V EPR/TPE-insulated control cores per BS 6708 | Every shipping drum
Routine test | Conductor, screen & armour DC resistance — Max. 15.4 Ω/km (1.34 mm²) or 22.1 Ω/km (0.93 mm²) on conductors; 37.3 / 44.7 Ω/km on 3 screens in parallel; 4.50–5.40 Ω/km on armour | Every shipping drum
Sample test | Chloroprene sheath flame & oil resistance — Heavy-duty PCP outer sheath tested for deep underground gassy/dusty mining service per BS 6708 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · BS 6708 · TYPE 506 / 512 / 518 / 524 · 320/550V
Supply | Delivery form: Export seaworthy fumigated wooden drums
Supply | Lengths: Standard drum lengths or custom cut harness lengths
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None