## Request a quote
Request a quotation for BS 6708 Type 62 / 63 / 64
Application engineer · BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-62-63-64-armoured-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type 62, Type 63 & Type 64 Screened Armoured Mining Cable – Dimensions, armour & electrical (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-62-63-64-armoured-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Type · nominal CSA mm² | Conductor stranding | Cond. Ø mm | Insul. Ø mm | Screen Ø mm | Inner sh. Ø mm | Min. OD mm | Max. OD mm | Min. R mm | Max. pull kgf | Mass ≈ kg/km | Cu wt kg/km | Current (25 °C) A | Cond. res. Ω/km | Screens res. Ω/km | Armour res. Ω/km | V-drop mV/A/m
| Type 62 · 2×4 | 56/0.30 | 2.6 | 4.8 | 6 | 16.2–18.2 | 23.9 | 26.4 | 270 | 48 | 1080 | 132 | 28 | 5.09 | 5.5 | 4.91 | 12.38
| Type 63 · 3×4 | 56/0.30 | 2.6 | 4.8 | 6 | 17.1–19.1 | 24.8 | 27.3 | 280 | 72 | 1230 | 200 | 28 | 5.09 | 3.9 | 4.63 | 10.72
| Type 64 · 4×4 | 56/0.30 | 2.6 | 4.8 | 6 | 18.7–20.7 | 26.4 | 29.9 | 290 | 96 | 1400 | 264 | 28 | 5.09 | 2.8 | 4.16 | 10.72
All three types have a reactance of 0.119 Ω/km at 50 Hz (0.143 Ω/km at 60 Hz) and a minimum insulation resistance of 590 MΩ·km at 20 °C.

## Technical data
BS 6708 Type 62, Type 63 & Type 64 Screened Armoured Mining Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-62-63-64-armoured-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 640/1,100 V (2.5 kV AC core test voltage)
Key data | Core layout | 2/3/4 × 4 mm² (Type 62 (2C) · 63 (3C) · 64 (4C))
Key data | Overall Ø | 23.9–29.9 mm (1,080–1,400 kg/km · 28 A)
Key data | Max. conductor T | +90 °C (EPR insulation (+85 °C sheath))
Key data | Min. operating T | −25 °C (Heavy-duty chloroprene (PCP))
Key data | Min. bend radius | 270–290 mm (48–96 kgf max pulling tension)
Electrical | Rated voltage (U0/U) | 640/1,100 V AC (U0/U)
Electrical | AC test voltage | 2.5 kV AC dielectric test on all screened cores
Electrical | Current rating (25 °C) | 28 A continuous current rating at 25 °C ambient (4 mm² Class 5 tinned copper)
Electrical | Conductor, screen & armour DC res. | 5.09 Ω/km max. conductor DC res. · 5.5 / 3.9 / 2.8 Ω/km max. parallel screen res. (Types 62/63/64) · 4.91 / 4.63 / 4.16 Ω/km max. armour res. at 20 °C
Electrical | Reactance, IR & voltage drop | 0.119 Ω/km (50 Hz) / 0.143 Ω/km (60 Hz) reactance · ≥ 590 MΩ·km insulation resistance at 20 °C · 12.38 mV/A/m (Type 62) / 10.72 mV/A/m (Types 63/64) voltage drop
Thermal | Max. conductor temperature | +90 °C maximum continuous conductor temperature (EPR insulation)
Thermal | Operating temperature range | −25 °C to +85 °C ambient installation / service range (current ratings referenced at 25 °C)
Mechanical | Minimum bending radius | 270 mm (Type 62), 280 mm (Type 63), 290 mm (Type 64) minimum bending radius (~10 × maximum OD)
Mechanical | Maximum pulling tension | 48 kgf (Type 62 2×4 mm²), 72 kgf (Type 63 3×4 mm²), 96 kgf (Type 64 4×4 mm²) maximum pulling tension
Mechanical | Screens, bedding & wire armour | Individually composite copper/nylon braided screened cores (Ø 6.00 mm) + rubber inner bedding sheath (Ø 16.2–20.7 mm) + galvanized steel pliable wire armour + heavy-duty PCP outer sheath
Resistance | Flame retardance | Flame retardant polychloroprene outer sheath to BS 6708 / BS EN 60332-1-2
Resistance | Crush & mine environment | Dual metallic protection (individual core screens + pliable steel wire armour) resists roadway rockfall, crushing, oil and moisture
Standards | Standards compliance | BS 6708 (Types 62, 63, 64); IEC 60228 Class 5; BS 7655
Standards | Designated duty | 640/1,100 V coalface lighting, remote control, interlock, signalling and auxiliary power circuits
Identification | Core identification | Coloured textile separator tape over EPR core insulation beneath individual composite tinned-copper/nylon braid screens
Identification | Outer sheath | Heavy-duty black chloroprene (PCP) outer sheath

## Construction
BS 6708 Type 62, Type 63 & Type 64 Screened Armoured Mining Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-62-63-64-armoured-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 4 mm² flexible conductors | Electrolytic stranded tinned copper wire, IEC 60228 Class 5 (56/0.30 mm, Ø 2.60 mm) | IEC 60228 Class 5
2 | Core insulation | EPR (ethylene-propylene rubber) to Ø 4.80 mm over each 4 mm² conductor | BS 7655 / BS 6708
3 | Identification tape | Coloured textile tape applied over EPR insulation for core identification
4 | Individual composite screens | Tinned copper and nylon braided screen over every core (Ø 6.00 mm; 2.8 to 5.5 Ω/km combined parallel resistance)
5 | Elastomeric cradle | Central elastomeric cradle around which the screened cores are laid up in contact
6 | Inner bedding sheath | Rubber-based inner bedding sheath extruded over laid-up screened cores (Ø 16.2 to 20.7 mm)
7 | Pliable wire armour (PWA) | Galvanized steel pliable wire armour (4.16 to 4.91 Ω/km DC resistance at 20 °C) | BS 6708 PWA
8 | Outer sheath | Heavy-duty flame-retardant polychloroprene (chloroprene / PCP) outer sheath, black | BS 6708 / BS 7655 EM2
| BS 6708 Type 62 · 2×4 mm² | 2 individually screened 4 mm² cores + rubber inner sheath + galvanized steel PWA + PCP outer sheath (23.9–26.4 mm OD, 1,080 kg/km)
| BS 6708 Type 63 · 3×4 mm² | 3 individually screened 4 mm² cores + rubber inner sheath + galvanized steel PWA + PCP outer sheath (24.8–27.3 mm OD, 1,230 kg/km)
| BS 6708 Type 64 · 4×4 mm² | 4 individually screened 4 mm² cores + rubber inner sheath + galvanized steel PWA + PCP outer sheath (26.4–29.9 mm OD, 1,400 kg/km)

## Quality and supply
BS 6708 Type 62, Type 63 & Type 64 Screened Armoured Mining Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-62-63-64-armoured-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage dielectric test — 2.5 kV AC applied between each 4 mm² conductor and its individual composite screen/armour | Every drum
Routine test | Conductor, screen & armour DC resistance check — ≤ 5.09 Ω/km conductor; ≤ 5.5 / 3.9 / 2.8 Ω/km parallel screens; ≤ 4.91 / 4.63 / 4.16 Ω/km armour at 20 °C | Every drum
Sample test | Insulation resistance verification — ≥ 590 MΩ·km at 20 °C on all EPR-insulated 4 mm² cores | Every drum
Sample test | Flame retardance test — Self-extinguishing heavy-duty chloroprene outer sheath per BS 6708 / BS EN 60332-1-2 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · BS 6708 TYPE 62 (or TYPE 63 / TYPE 64) · 640/1100 V · [2x4 / 3x4 / 4x4] · PCP
Supply | Delivery form: Heat-treated seaworthy wooden drums lagged with solid timber battens
Supply | Lengths: Custom cut-to-length reels per coalface lighting/control schedule
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None