## Request a quote
Request a quotation for BS 6708 Type 621 (3.8/6.6 kV)
Application engineer · BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-621-armoured-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type 621 Armoured Power Cable (3.8/6.6 kV) – Dimensions & electrical (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-621-armoured-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation 4 Cores | Core CSA mm² | Stranding n/mm | Cond. Ø mm | EPR wall mm | Inner wall mm | Inner min Ø mm | Inner max Ø mm | Armour n/mm | Outer wall mm | Min. OD mm | Max. OD mm | Min. bend mm | Current 25 °C A | Cond. DC 20 °C Ω/km | Armour DC 20 °C Ω/km | Cu mass kg/km | Mass ≈ kg/km
| Type 621 · 4 × 35 mm² | 35 | 276/0.40 | 8.4 | 5 | 3.8 | 53.8 | 56.8 | 7/0.90 | 6 | 71.2 | 75.2 | 752 | 135 | 0.565 | 0.7 | 1350 | 8900
| Type 621 · 4 × 50 mm² | 50 | 396/0.40 | 10.1 | 5 | 5 | 60.5 | 63.5 | 7/1.25 | 6.3 | 81 | 85.3 | 853 | 170 | 0.393 | 0.5 | 1950 | 11100
| Type 621 · 4 × 70 mm² | 70 | 360/0.50 | 11.9 | 5 | 5 | 65.6 | 69.4 | 7/1.25 | 7 | 87.1 | 91.4 | 914 | 205 | 0.277 | 0.43 | 2700 | 13000
| Type 621 · 4 × 95 mm² | 95 | 475/0.50 | 13.9 | 5 | 5 | 70.7 | 74.5 | 7/1.25 | 7.5 | 93.2 | 97.5 | 975 | 250 | 0.21 | 0.39 | 3700 | 14050
| Type 621 · 4 × 120 mm² | 120 | 608/0.50 | 15.5 | 5 | 5 | 74.3 | 78.1 | 7/1.25 | 7.8 | 97.4 | 101.7 | 1017 | 295 | 0.164 | 0.38 | 4650 | 20600
| Type 621 · 4 × 150 mm² | 150 | 756/0.50 | 17.2 | 5 | 5 | 79.2 | 83.2 | 7/1.25 | 8.3 | 103.3 | 107.6 | 1076 | 320 | 0.132 | 0.35 | 5800 | 22000
All 4 cores (3 phase + 1 pilot/earth) have equal conductor cross-sections and 5.0 mm nominal EPR insulation.
Minimum bending radius is 10 × Maximum Overall Diameter across all sizes.

## Technical data
BS 6708 Type 621 Armoured Power Cable (3.8/6.6 kV) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-621-armoured-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3,800/6,600 V (15 kV AC routine test)
Key data | Core arrangement | 4C + Pliable PWA (3 phase + 1 pilot/earth)
Key data | Size range | 4×35–4×150 mm² (6 standard sizes)
Key data | Ampacity (25 °C) | 135–320 A (Continuous ambient rating)
Key data | Operating temp. | −25 to +85 °C (5.0 mm EPR / PCP)
Key data | Min. bend radius | 10 × OD (752+) (Pliable 7-wire armour)
Electrical | Rated voltage U0/U | 3,800/6,600 V AC (3.8/6.6 kV) · 15 kV routine AC test voltage
Electrical | Current rating (25 °C) | 135 A (4×35 mm²) to 320 A (4×150 mm²) continuous at 25 °C ambient
Electrical | Conductor & armour DC resistance | Conductors: 0.565 to 0.132 Ω/km at 20 °C · Pliable steel armour: 0.70 to 0.35 Ω/km at 20 °C
Thermal | Ambient temperature range | −25 °C to +85 °C
Thermal | Max. conductor temperature | +90 °C continuous EPR operating temperature
Mechanical | Min. bending radius | 752 mm (4×35 mm²) to 1,076 mm (4×150 mm²) (10 × max OD)
Mechanical | Armour & sheaths | 3.8–5.0 mm rubber inner sheath + 7/0.90 or 7/1.25 mm pliable galvanised steel armour + 6.0–8.3 mm heavy-duty chloroprene outer sheath
Resistance | Crush & impact protection | 7-wire stranded galvanised steel pliable wire armour (7/0.90 or 7/1.25 mm) resists rockfall and quarry impact
Resistance | Flame, oil & environment | 6.0–8.3 mm heavy-duty chloroprene (PCP) outer sheath for deep gassy/dusty mines and surface quarries
Standards | Construction standard | BS 6708 (Medium-voltage pliable-armoured mining cables)
Standards | Conductor & insulation | IEC 60228 Class 5 tinned copper · 5.0 mm nominal EPR medium-voltage dielectric
Standards | Routine voltage test | 15 kV AC routine dielectric test on all four 3.8/6.6 kV cores
Identification | Type designation | BS 6708 Type 621 (3,800/6,600 V · 4 unscreened cores + pliable armour)
Identification | Core arrangement | Three phase cores + one pilot/earth core, all unscreened and equal in cross-section (35–150 mm²)

## Construction
BS 6708 Type 621 Armoured Power Cable (3.8/6.6 kV) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-621-armoured-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase & pilot/earth conductors (4) | Electrolytic stranded tinned copper wire, IEC 60228 Class 5 (4×35 to 4×150 mm²) | IEC 60228 Class 5
2 | Medium-voltage EPR insulation | Ethylene propylene rubber (EPR, 5.0 mm nominal radial wall on all sizes, 15 kV AC routine test) | BS 6708 (3.8/6.6 kV)
3 | Rubber bedding & inner sheath | Rubber-based inner sheath compound (3.8 mm on 4×35 mm²; 5.0 mm on 4×50–4×150 mm²) | BS 6708
4 | Pliable galvanised steel wire armour | Stranded galvanised steel pliable armour (7/0.90 mm on 4×35 mm²; 7/1.25 mm on 4×50–4×150 mm², 0.35–0.70 Ω/km) | BS 6708
5 | Heavy-duty chloroprene outer sheath | Heavy-duty flame-retardant polychloroprene (chloroprene / PCP, 6.0 to 8.3 mm radial thickness) | BS 6708
| BS 6708 Type 621 (4×35–4×150 mm² · Unscreened) | 3 unscreened phase cores + 1 unscreened pilot/earth core + pliable galvanised steel wire armour
| Screened Alternative: BS 6708 Type 630 / 631 | For 3,800/6,600 V pliable-armoured cables with individually copper/nylon braided-screened phase cores, specify Type 630 or Type 631

## Quality and supply
BS 6708 Type 621 Armoured Power Cable (3.8/6.6 kV) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-621-armoured-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 15 kV AC high-voltage dielectric test — 15 kV AC routine voltage withstand test on 3,800/6,600 V 5.0 mm EPR cores per BS 6708 | Every shipping drum
Routine test | Conductor & pliable armour DC resistance — Max. 0.565 to 0.132 Ω/km on Class 5 tinned copper cores; 0.70 to 0.35 Ω/km on pliable GSW armour at 20 °C | Every shipping drum
Sample test | Chloroprene sheath flame, oil & mechanical test — Heavy-duty PCP outer sheath tested for deep underground and surface mining service per BS 6708 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · BS 6708 · TYPE 621 · 3800/6600V · 4 x [mm²]
Supply | Delivery form: Export seaworthy fumigated wooden drums matched to 10 × OD bend radius
Supply | Lengths: Standard drum lengths or custom cut lengths per mine roadway schedule
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None