## Request a quote
Request a quotation for BS 6708 Type 630 & Type 631 (3.8/6.6 kV)
Application engineer · BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-630-631-mv-armoured-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type 630 & 631 MV Armoured Cable (3.8/6.6 kV) – Dimensions & mechanical (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-630-631-mv-armoured-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation BS 6708 Type | Phase mm² | Phase strand n/mm | Phase Ø mm | EPR wall mm | Earth core mm² (strand · Ø) | Inner wall mm | Inner min Ø mm | Inner max Ø mm | Armour n/mm | Outer wall mm | Min. OD mm | Max. OD mm | Min. bend mm | Cu mass kg/km | Mass ≈ kg/km
| Type 630 · 3 × 35 mm² | 35 | 276/0.40 | 8.4 | 5 | — | 3.8 | 53.1 | 56.1 | 7/0.90 | 6 | 70.5 | 74.5 | 894 | 1010 | 8400
| Type 630 · 3 × 50 mm² | 50 | 396/0.40 | 10.1 | 5 | — | 3.8 | 56 | 60 | 7/0.90 | 6.3 | 75 | 79.3 | 952 | 1450 | 9850
| Type 630 · 3 × 70 mm² | 70 | 360/0.50 | 11.9 | 5 | — | 5 | 63 | 67 | 7/1.25 | 6.8 | 80.6 | 84.9 | 1019 | 2020 | 12050
| Type 630 · 3 × 95 mm² | 95 | 475/0.50 | 13.9 | 5 | — | 5 | 72.3 | 72.3 | 7/1.25 | 7.3 | 90.6 | 94.9 | 1139 | 2750 | 13850
| Type 630 · 3 × 120 mm² | 120 | 608/0.50 | 15.5 | 5 | — | 5 | 75.5 | 75.5 | 7/1.25 | 7.6 | 94.4 | 98.7 | 1185 | 3460 | 19200
| Type 630 · 3 × 150 mm² | 150 | 756/0.50 | 17.2 | 5 | — | 5 | 80 | 80 | 7/1.25 | 8 | 99.6 | 103.9 | 1247 | 4330 | 21200
| Type 631 · 3 × 50 + 35E | 50 | 396/0.40 | 10.1 | 5 | 1×35 (276/0.40 · 8.40 Ø) | 5 | 65.4 | 69.2 | 7/0.90 | 6.9 | 86.7 | 91 | 1092 | 2100 | 12100
| Type 631 · 3 × 70 + 50E | 70 | 360/0.50 | 11.9 | 5 | 1×50 (396/0.40 · 10.10 Ø) | 5 | 70.5 | 74.3 | 7/1.25 | 7.4 | 92.8 | 97.1 | 1166 | 3100 | 14250
All phase cores (and the unscreened earth core in Type 631) have 5.0 mm nominal radial EPR insulation wall thickness.
Minimum bending radius is 12 × Maximum Overall Diameter across all Type 630 and Type 631 configurations.

## Electrical parameters
BS 6708 Type 630 & 631 MV Armoured Cable (3.8/6.6 kV) – Electrical parameters (25 °C) (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-630-631-mv-armoured-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Designation BS 6708 Type | Current rating A (25 °C) | Phase DC 20 °C Ω/km | Earth DC 20 °C Ω/km | Armour DC 20 °C Ω/km | 3 screens par. Ω/km
Type 630 · 3 × 35 mm² | 135 | 0.565 | — | 0.76 | 1
Type 630 · 3 × 50 mm² | 170 | 0.393 | — | 0.71 | 0.88
Type 630 · 3 × 70 mm² | 205 | 0.277 | — | 0.46 | 0.72
Type 630 · 3 × 95 mm² | 250 | 0.21 | — | 0.43 | 0.78
Type 630 · 3 × 120 mm² | 295 | 0.164 | — | 0.41 | 0.62
Type 630 · 3 × 150 mm² | 320 | 0.132 | — | 0.39 | 0.67
Type 631 · 3 × 50 + 35E | 170 | 0.393 | 0.565 | 0.45 | 0.45
Type 631 · 3 × 70 + 50E | 205 | 0.277 | 0.393 | 0.42 | 0.42
In Type 630, earth fault current is carried by the 3 phase core screens in parallel (0.62–1.00 Ω/km) plus the pliable steel wire armour (0.39–0.76 Ω/km). Type 631 adds a dedicated 35 or 50 mm² copper earth core.

## Technical data
BS 6708 Type 630 & 631 MV Armoured Cable (3.8/6.6 kV) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-630-631-mv-armoured-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3,800/6,600 V (15 kV AC routine test)
Key data | Core arrangement | 3P (scr) ± E (630 (3C) · 631 (3C+E))
Key data | Phase size range | 35–150 mm² (8 standard configurations)
Key data | Ampacity (25 °C) | 135–320 A (Continuous ambient rating)
Key data | Operating temp. | −25 to +85 °C (5.0 mm EPR + twin sheaths)
Key data | Min. bend radius | 12 × OD (894+) (7/0.90 or 7/1.25 armour)
Electrical | Rated voltage U0/U | 3,800/6,600 V (3.8/6.6 kV) AC · 15 kV routine AC test voltage
Electrical | Current rating (25 °C) | 135 to 320 A continuous at 25 °C ambient (Type 630) · 170 to 205 A (Type 631)
Electrical | Screen & armour DC resistance | 3 screens in parallel: 0.42–1.00 Ω/km at 20 °C · Pliable GSW armour: 0.39–0.76 Ω/km at 20 °C
Thermal | Ambient temperature range | −25 °C to +85 °C
Thermal | Max. conductor temperature | +90 °C continuous EPR operating temperature (250 °C short-circuit)
Mechanical | Min. bending radius | 12 × Maximum Overall Diameter (894 to 1,247 mm across 35–150 mm²)
Mechanical | Pliable wire armour & sheaths | 3.8–5.0 mm rubber inner sheath + 7/0.90 mm or 7/1.25 mm pliable galvanised steel wire armour + 6.0–8.0 mm heavy-duty PCP outer sheath
Resistance | Crush & impact protection | Pliable galvanised steel wire armour between thick elastomer sheaths withstands rockfall and roadway crush
Resistance | Flame, oil & gassy mine environment | Heavy-duty chloroprene (PCP) outer sheath (6.0–8.0 mm wall) for deep mines with explosive gas and coal dust
Standards | Construction standard | BS 6708 (3.8/6.6 kV screened pliable-armoured mining cables — Type 630 & Type 631)
Standards | Conductor & insulation | IEC 60228 Class 5 flexible tinned copper · 5.0 mm EPR insulation · individual Cu/nylon braided phase screens
Standards | Routine voltage test | 15 kV AC routine dielectric test on all 3.8/6.6 kV cores
Identification | Type 630 vs Type 631 | Type 630: 3 individually screened phase cores · Type 631: 3 individually screened phase cores + 1 unscreened 5.0 mm EPR earth core
Identification | Core identification | Coloured textile separator tape over EPR insulation under individual tinned-copper/nylon braided screens

## Construction
BS 6708 Type 630 & 631 MV Armoured Cable (3.8/6.6 kV) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-630-631-mv-armoured-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible phase conductors (3) + earth core (Type 631) | Electrolytic stranded tinned copper wire, IEC 60228 Class 5 (35 to 150 mm² phases; 35 or 50 mm² earth on Type 631) | IEC 60228 Class 5
2 | 5.0 mm EPR medium-voltage insulation | Ethylene propylene rubber (EPR) dielectric, 5.0 mm nominal radial wall on all phase cores (and Type 631 earth core), 15 kV AC tested | BS 6708 (15 kV test)
3 | Coloured textile identification tape | Colour-coded textile separator tape over EPR insulation under each core screen | BS 6708
4 | Composite copper / nylon braided phase screen | Tinned copper wire and nylon braided screen over each of the 3 phase cores (0.42–1.00 Ω/km for 3 screens in parallel) | BS 6708
5 | Rubber inner bedding sheath | Extruded rubber inner sheath compound (3.8 mm on 3×35 & 3×50; 5.0 mm on 3×70 to 3×150 and Type 631) | BS 6708
6 | Pliable galvanised steel wire armour | 7/0.90 mm (3×35, 3×50, 3×50+35) or 7/1.25 mm (3×70–3×150, 3×70+50) stranded galvanised steel pliable armour (0.39–0.76 Ω/km) | BS 6708
7 | Heavy-duty chloroprene outer sheath | Heavy-duty flame-retardant polychloroprene (chloroprene / PCP, 6.0 to 8.0 mm radial wall) | BS 6708
| BS 6708 Type 630 (3×35 – 3×150 mm²) | 3 individually copper/nylon braided-screened 5.0 mm EPR phase cores + rubber inner sheath + pliable GSW armour + PCP sheath
| BS 6708 Type 631 (3×50+35 & 3×70+50 mm²) | 3 individually screened 5.0 mm EPR phase cores + 1 unscreened 5.0 mm EPR earth core (35 or 50 mm²) + pliable GSW armour + PCP sheath

## Quality and supply
BS 6708 Type 630 & 631 MV Armoured Cable (3.8/6.6 kV) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-630-631-mv-armoured-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 15 kV AC high-voltage dielectric test — 15 kV AC routine voltage withstand test on 3.8/6.6 kV 5.0 mm EPR cores per BS 6708 | Every shipping drum
Routine test | Phase, earth, screen & armour DC resistance — Verified on all phase conductors, earth conductor (Type 631), 3 parallel screens and pliable GSW armour at 20 °C | Every shipping drum
Sample test | Heavy-duty PCP sheath flame, oil & mechanical test — 6.0–8.0 mm chloroprene outer sheath tested for deep underground mining service per BS 6708 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · BS 6708 · TYPE 630 / TYPE 631 · 3800/6600V
Supply | Delivery form: Export seaworthy fumigated wooden drums matched to 12 × OD bend radius
Supply | Lengths: Standard drum lengths or custom cut lengths per mine roadway schedule
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None