## Request a quote
Request a quotation for BS 6708 Type 730 (3.8/6.6 kV)
Application engineer · BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-730-mv-trailing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type 730 MV Trailing Cable (3,800/6,600 V) – Dimensions & electrical (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-730-mv-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation mm² | Phase mm² | Phase strand n/mm | Phase Ø mm | EPR wall mm | Central earth mm² (strand · Ø) | Outer wall mm | Min. OD mm | Max. OD mm | Min. bend mm | Current 25 °C A | Phase DC 20 °C Ω/km | 3 scr + earth Ω/km | Cu mass kg/km | Mass ≈ kg/km
| 3 × 35 | 35 | 276/0.40 | 8.4 | 5 | — (3 screens) | 6 | 57.5 | 60.5 | 605 | 135 | 0.565 | 0.81 | 1300 | 4800
| 3 × 50 | 50 | 396/0.40 | 10.1 | 5 | — (3 screens) | 6.3 | 62 | 65 | 650 | 170 | 0.393 | 0.78 | 1800 | 5900
| 3 × 70 | 70 | 360/0.50 | 11.9 | 5 | — (3 screens) | 6.8 | 67.5 | 71.4 | 714 | 205 | 0.277 | 0.55 | 2500 | 7100
| 3 × 95 | 95 | 475/0.50 | 13.9 | 5 | — (3 screens) | 7.3 | 73.1 | 76.9 | 769 | 250 | 0.21 | 0.42 | 3250 | 8500
| 3 × 120 + 16 | 120 | 608/0.50 | 15.5 | 5 | 1×16 (126/0.40 · 5.50 Ø) | 7.6 | 76.9 | 80.9 | 809 | 295 | 0.164 | 0.32 | 4200 | 9950
| 3 × 150 + 16 | 150 | 756/0.50 | 17.2 | 5 | 1×16 (126/0.40 · 5.50 Ø) | 8 | 82.1 | 86 | 860 | 320 | 0.132 | 0.26 | 5000 | 11400
On 3×35 to 3×95 mm², the three tinned-copper/nylon braided phase screens laid in mutual contact form the protective earth path (0.42–0.81 Ω/km). On 3×120+16 and 3×150+16 mm², a central bare 1×16 mm² (126/0.40 mm) tinned copper earth conductor is laid in contact with all three screens.
Minimum bending radius is 10 × Maximum Overall Diameter across all sizes.

## Technical data
BS 6708 Type 730 MV Trailing Cable (3,800/6,600 V) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-730-mv-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3,800/6,600 V (15 kV AC routine test)
Key data | Core arrangement | 3P (scr) ± 16E (Mutual-contact screens)
Key data | Phase size range | 35–150 mm² (6 standard sizes)
Key data | Ampacity (25 °C) | 135–320 A (Continuous ambient rating)
Key data | Operating temp. | −25 to +85 °C (5.0 mm EPR + PCP)
Key data | Min. bend radius | 10 × OD (605+) (Unarmoured flexible)
Electrical | Rated voltage U0/U | 3,800/6,600 V (3.8/6.6 kV) AC · 15 kV routine AC test voltage
Electrical | Current rating (25 °C) | 135 A (35 mm²) to 320 A (150 mm²) continuous at 25 °C ambient
Electrical | Phase & screen/earth DC resistance | Phase conductors: 0.565–0.132 Ω/km at 20 °C · 3 screens + earth in parallel: 0.81–0.26 Ω/km at 20 °C
Thermal | Ambient temperature range | −25 °C to +85 °C
Thermal | Max. conductor temperature | +90 °C continuous EPR operating temperature (250 °C short-circuit)
Mechanical | Min. bending radius | 10 × Maximum Overall Diameter (605 mm on 3×35 mm² to 860 mm on 3×150+16 mm²)
Mechanical | Bedding & outer sheath | Rubber bedding compound + 6.0 to 8.0 mm heavy-duty chloroprene (PCP) outer sheath (57.5–86.0 mm OD)
Resistance | Trailing abrasion & tear resistance | Unarmoured flexible construction with 6.0–8.0 mm heavy-duty chloroprene jacket resists rough quarry & mine floor drag
Resistance | Flame, oil & water | Heavy-duty flame-retardant and oil-resistant chloroprene (PCP) outer sheath for wet underground & surface mining
Standards | Construction standard | BS 6708 (3,800/6,600 V screened non-armoured mining trailing cable — Type 730)
Standards | Conductor & insulation | IEC 60228 Class 5 flexible tinned copper · 5.0 mm EPR insulation · composite Cu/nylon braided core screens
Standards | Routine voltage test | 15 kV AC routine dielectric test on all 3,800/6,600 V phase cores
Identification | Core identification | Coloured textile separator tape over EPR insulation under each tinned-copper/nylon braided phase screen
Identification | Central earth conductor | 3×35 to 3×95 mm²: 3 screened cores · 3×120+16 & 3×150+16 mm²: adds central bare 16 mm² (126/0.40 mm) tinned copper earth

## Construction
BS 6708 Type 730 MV Trailing Cable (3,800/6,600 V) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-730-mv-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible phase conductors (3) | Electrolytic stranded tinned copper wire, IEC 60228 Class 5 (35 to 150 mm², 276/0.40 to 756/0.50 mm) | IEC 60228 Class 5
2 | 5.0 mm EPR medium-voltage insulation | Ethylene propylene rubber (EPR) dielectric, 5.0 mm nominal radial wall across all sizes (15 kV AC routine test) | BS 6708 (15 kV test)
3 | Coloured textile identification tape | Colour-coded textile separator tape over EPR insulation under each core screen | BS 6708
4 | Composite copper / nylon braided phase screen | Tinned copper wire and nylon braided screen over each phase core, laid up in mutual contact (0.26–0.81 Ω/km combined with earth) | BS 6708
5 | Central bare earth conductor (120 & 150 mm²) | 1×16 mm² (126/0.40 mm, 5.50 mm Ø) bare Class 5 tinned copper earth conductor in contact with the 3 core screens on 3×120+16 and 3×150+16 | BS 6708
6 | Rubber inner bedding | Extruded elastomeric rubber bedding filling interstices and cushioning the screened core assembly | BS 6708
7 | Heavy-duty chloroprene outer sheath | Heavy-duty flame-retardant polychloroprene (chloroprene / PCP, 6.0 to 8.0 mm radial wall) | BS 6708
| BS 6708 Type 730 · 3×35 to 3×95 mm² | 3 individually copper/nylon braided-screened 5.0 mm EPR phase cores laid in mutual contact (0.42–0.81 Ω/km screen earth path)
| BS 6708 Type 730 · 3×120+16 & 3×150+16 mm² | 3 individually screened 5.0 mm EPR phase cores + central 1×16 mm² (126/0.40 mm) bare copper earth core (0.26–0.32 Ω/km)

## Quality and supply
BS 6708 Type 730 MV Trailing Cable (3,800/6,600 V) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-730-mv-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 15 kV AC high-voltage dielectric test — 15 kV AC routine voltage withstand test on 3,800/6,600 V 5.0 mm EPR phase cores per BS 6708 | Every shipping drum
Routine test | Phase conductor & parallel screens/earth DC resistance — Max. 0.565–0.132 Ω/km on phase conductors and 0.81–0.26 Ω/km on 3 screens + earth in parallel at 20 °C | Every shipping drum
Sample test | Heavy-duty PCP sheath flame, oil & tear test — 6.0–8.0 mm chloroprene outer sheath tested for rough movable mining service per BS 6708 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · BS 6708 · TYPE 730 · 3800/6600V
Supply | Delivery form: Export seaworthy fumigated wooden drums matched to 10 × OD bend radius
Supply | Lengths: Standard drum lengths or custom cut trailing lengths
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None