## Request a quote
Request a quotation for BS 6708 Type 830
Application engineer · mining & trailing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-830-6-35-11kv-screened-open-cast-excavator-trailing-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type 830 6.35/11 kV Excavator Trailing Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-830-6-35-11kv-screened-open-cast-excavator-trailing-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on BS 6708 Type 830 / BS EN 60228. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| BS 6708 Type 830 3×95 + 1×16 mm² | 3 × 95 mm² + 1 × 16 mm² (E) | Class 5 tinned Cu | 71.5 | 7450 | 42.5 | 715 | BS 6708 Type 830 Construction Schedule (-25 to +90 °C)
| BS 6708 Type 830 3×120 + 1×16 mm² | 3 × 120 mm² + 1 × 16 mm² (E) | Class 5 tinned Cu | 75.8 | 8620 | 54 | 760 | BS 6708 Type 830 Construction Schedule (-25 to +90 °C)
| BS 6708 Type 830 3×150 + 1×25 mm² | 3 × 150 mm² + 1 × 25 mm² (E) | Class 5 tinned Cu | 81.2 | 10180 | 67.5 | 815 | BS 6708 Type 830 Construction Schedule (-25 to +90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per BS 6708 Type 830 / BS EN 60228.

## Electrical, optical & thermal p
BS 6708 Type 830 6.35/11 kV Excavator Trailing Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-830-6-35-11kv-screened-open-cast-excavator-trailing-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on BS 6708 Type 830 / BS EN 60228. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 95 mm² + 1 × 16 mm² (E) | 0.21 | 6.35/11 kV (265 A) | -25 to +90 °C
3 × 120 mm² + 1 × 16 mm² (E) | 0.164 | 6.35/11 kV (305 A) | -25 to +90 °C
3 × 150 mm² + 1 × 25 mm² (E) | 0.132 | 6.35/11 kV (350 A) | -25 to +90 °C
Every production length undergoes routine conductor DC resistance, high-voltage Spark/AC dielectric or OTDR continuity and dimensional verification.

## Technical data
BS 6708 Type 830 6.35/11 kV Excavator Trailing Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-830-6-35-11kv-screened-open-cast-excavator-trailing-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on BS 6708 Type 830 / BS EN 60228. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 6.35/11 kV (6.35/11 kV open-cast shovel & dragline)
Key data | Operating temp. | -25 to +90 °C (Continuous mining & industrial duty)
Key data | Min. bend radius | 10 × OD (Fixed installation / dynamic routing)
Key data | Core / conductor | 3×70–185 mm² Cu (Class 5 tinned Cu + central earth)
Key data | Outer protection | Heavy-Duty PCP (Tear- & oil-resistant PCP rubber jacket)
Key data | Standard | BS 6708 T830 (BS 6708 Type 830 / BS EN 60228)
Electrical | Rated voltage / transmission duty | 6.35/11 kV (BS 6708 Type 830 / BS EN 60228)
Electrical | Core / conductor construction | Phase Conductors (3×120 mm²) — IEC 60228 Class 5 flexible annealed tinned copper + semicon screen
Electrical | Primary dielectric / buffering | 6.35/11 kV EPR Insulation (7.5 mm) — Thick high-dielectric EPR phase insulation (Red, Yellow & Brown)
Thermal | Continuous operating temperature | -25 to +90 °C (mining & industrial service)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per BS 6708 Type 830 / BS EN 60228
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Heavy-Duty Outer Sheath (PCP) — Black tear-, oil- and weather-resistant polychloroprene rubber sheath
Mechanical | Minimum bending radius | 10 × OD
Mechanical | Crush, impact & abrasion duty | Heavy-duty mining rock-cut, impact and tensile protection per BS 6708 Type 830 / BS EN 60228
Resistance | Flame retardancy & mine fire safety | Self-extinguishing / flame-retardant mining jacket per BS 6708 Type 830 / BS EN 60228
Resistance | Mine water, oil & chemical resistance | Resistant to acidic mine water, hydraulic oils and abrasion per BS 6708 Type 830 / BS EN 60228
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | BS 6708 Type 830 / BS EN 60228
Standards | Flame & environmental test standards | IEC 60332 / MSHA / EN 60794 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | BS 6708 Type 830
Identification | Sheath colour & metre marking | Continuous metre-marked black mining outer sheath
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
BS 6708 Type 830 6.35/11 kV Excavator Trailing Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-830-6-35-11kv-screened-open-cast-excavator-trailing-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on BS 6708 Type 830 / BS EN 60228. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase Conductors (3×120 mm²) | IEC 60228 Class 5 flexible annealed tinned copper + semicon screen
2 | 6.35/11 kV EPR Insulation (7.5 mm) | Thick high-dielectric EPR phase insulation (Red, Yellow & Brown)
3 | Composite Phase Braid Screen | Tinned copper wire and nylon fibre composite braid over each core
4 | Central Earth Conductor (1×16 mm²) | Uninsulated flexible tinned copper conductor in central interstice
5 | Heavy-Duty Outer Sheath (PCP) | Black tear-, oil- and weather-resistant polychloroprene rubber sheath
| BS 6708 Type 830 — Standard Mining Execution | Built to BS 6708 Type 830 / BS EN 60228 with phase conductors (3×120 mm²) and heavy-duty outer sheath (pcp)
| BS 6708 Type 830 — Custom Drum Length & Gland Kit | Available in custom shaft/roadway drum lengths or pre-terminated assemblies
| BS 6708 Type 830 — Routine & Flame Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & flame test report

## Quality and supply
BS 6708 Type 830 6.35/11 kV Excavator Trailing Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-830-6-35-11kv-screened-open-cast-excavator-trailing-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on BS 6708 Type 830 / BS EN 60228. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (BS 6708 Type 830 / BS EN 60228) — DC resistance at 20 °C / optical attenuation and outer diameter within BS 6708 Type 830 / BS EN 60228 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (BS 6708 Type 830 / BS EN 60228) — Zero dielectric breakdown and verified insulation resistance over full production length | Every manufactured drum length
Type test | Flame propagation, mechanical crush & thermal ageing qualification (BS 6708 Type 830 / BS EN 60228) — Verified flame retardancy, mechanical integrity and thermal endurance across -25 to +90 °C | Type qualification & periodic lot audit
Standard / approval | BS 6708 T830 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BS 6708 Type 830 BS 6708 T830 6.35/11 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel mine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shaft/reeling lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP