## Request a quote
Request a quotation for BS 6708 Type FS4 Flat Cable (640/1,100 V)
Application engineer · BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6708-type-fs4-flat-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6708 Type FS4 Flat Catenary Cable (640/1,100 V) – Dimensions & electrical (2)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-fs4-flat-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation BS 6708 Type | Core CSA mm² | Stranding n/mm | Cond. Ø mm | EPR wall mm | Sheath wall mm | Min. W × H mm | Max. W × H mm | Min. bend mm | Current 25 °C A | Cond. DC 20 °C Ω/km | Each screen Ω/km | Cu mass kg/km | Mass ≈ kg/km
| Type FS4 · 4 × 2.5 mm² | 2.5 | 50/0.25 | 2.1 | 1 | 3.8 | 29.8 × 12.4 | 31.8 × 14.4 | 100 | 28 | 7.82 | 7.4 | 160 | 450
| Type FS4 · 4 × 4 mm² | 4 | 50/0.30 | 2.7 | 1 | 3.8 | 32.2 × 13.3 | 34.1 × 15.3 | 120 | 37 | 4.85 | 8.48 | 230 | 550
Unlike circular BS 6708 trailing cables whose core screens touch each other, Type FS4 spaces all 4 braided cores (3 phase + 1 pilot) in a flat plane without contacting each other.
Screen DC resistance (7.40 Ω/km on 4×2.5 mm² and 8.48 Ω/km on 4×4 mm²) is specified per individual core screen at 20 °C.

## Technical data
BS 6708 Type FS4 Flat Catenary Cable (640/1,100 V) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-fs4-flat-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 640/1,100 V (3 kV AC routine test)
Key data | Core arrangement | 3P + 1P (Flat) (Non-contacting screens)
Key data | Standard sizes | 4×2.5 & 4×4 mm² (50/0.25 & 50/0.30 mm)
Key data | Ampacity (25 °C) | 28–37 A (Continuous catenary duty)
Key data | Operating temp. | −25 to +85 °C (1.0 mm EPR + 3.8 mm PCP)
Key data | Min. bend radius | 100–120 mm (Minor-axis catenary loop)
Electrical | Rated voltage U0/U | 640/1,100 V AC · 3 kV routine AC test voltage
Electrical | Current rating (25 °C) | 28 A (4×2.5 mm²) · 37 A (4×4 mm²) continuous at 25 °C ambient
Electrical | Conductor & screen DC resistance | Conductors: 7.82 Ω/km (2.5 mm²) / 4.85 Ω/km (4 mm²) · Each copper braid screen: 7.40 Ω/km (2.5 mm²) / 8.48 Ω/km (4 mm²)
Thermal | Ambient temperature range | −25 °C to +85 °C
Thermal | Max. conductor temperature | +90 °C continuous EPR operating temperature (250 °C short-circuit)
Mechanical | Min. bending radius | 100 mm (4×2.5 mm²) · 120 mm (4×4 mm²) on minor flat axis
Mechanical | Flat profile & sheath wall | 4 screened cores spaced parallel without contact in a 3.8 mm nominal heavy-duty chloroprene (PCP) flat outer sheath
Resistance | Catenary flexing & twist immunity | Flat parallel geometry eliminates axial corkscrewing on overhead monorail catenary carriers and loop systems
Resistance | Flame, oil & inter-core isolation | Heavy-duty chloroprene web separates each braided core screen while resisting flame, mineral oil and mine water
Standards | Construction standard | BS 6708 (640/1,100 V flat catenary mining power supply cable — Type FS4)
Standards | Conductor & insulation | IEC 60228 Class 5 flexible tinned copper (50/0.25 or 50/0.30 mm) · 1.0 mm EPR insulation · individual tinned Cu braid screen
Standards | Routine voltage test | 3,000 V (3 kV) AC routine dielectric test on all 4 cores
Identification | Core identification | Coloured textile separator tape over 1.0 mm EPR insulation under each tinned copper braid screen (3 phase + 1 pilot)
Identification | Screen separation | Each of the 4 tinned copper braided screens is electrically isolated from adjacent screens by the moulded PCP sheath web

## Construction
BS 6708 Type FS4 Flat Catenary Cable (640/1,100 V) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-fs4-flat-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase (3) & pilot (1) conductors | Electrolytic stranded tinned copper wire, IEC 60228 Class 5 (50/0.25 mm = 2.5 mm² or 50/0.30 mm = 4 mm²) | IEC 60228 Class 5
2 | 1.0 mm EPR core insulation | Ethylene propylene rubber (EPR) dielectric, 1.0 mm nominal radial wall (3 kV AC routine test) | BS 6708 (3 kV test)
3 | Coloured textile identification tape | Colour-coded textile tape over EPR insulation for phase and pilot identification | BS 6708
4 | Individual tinned copper braid screen | Tinned copper braided screen over each of the 4 cores (7.40 Ω/km on 2.5 mm²; 8.48 Ω/km on 4 mm²) | BS 6708
5 | Flat heavy-duty chloroprene outer sheath | Heavy-duty flame-retardant polychloroprene (PCP, 3.8 mm nominal radial wall) spacing all 4 screened cores parallel without mutual contact | BS 6708
| BS 6708 Type FS4 · 4 × 2.5 mm² | 3 phase + 1 pilot (50/0.25 mm) · 29.8×12.4 to 31.8×14.4 mm flat profile · 28 A · 450 kg/km
| BS 6708 Type FS4 · 4 × 4 mm² | 3 phase + 1 pilot (50/0.30 mm) · 32.2×13.3 to 34.1×15.3 mm flat profile · 37 A · 550 kg/km

## Quality and supply
BS 6708 Type FS4 Flat Catenary Cable (640/1,100 V) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6708-type-fs4-flat-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6708 · IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3 kV AC dielectric withstand test — 3,000 V AC routine voltage test on all 4 EPR-insulated cores per BS 6708 | Every shipping drum
Routine test | Conductor & individual screen DC resistance + screen isolation — Max. 7.82 / 4.85 Ω/km on conductors; max. 7.40 / 8.48 Ω/km on each copper braid screen; electrical non-contact between adjacent screens | Every shipping drum
Sample test | Chloroprene flat sheath flame, oil & flexing test — 3.8 mm heavy-duty PCP flat sheath tested for catenary flexing, oil and flame retardance per BS 6708 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · BS 6708 · TYPE FS4 · 640/1100V · 4 x [mm²]
Supply | Delivery form: Export seaworthy fumigated wooden drums
Supply | Lengths: Standard drum lengths or custom cut catenary loop lengths
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None