## Request a quote
Request a quotation for BS 6883 A
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for BS 6883 A.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6883-armoured-offshore-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6883 A rmoured Offshore Power Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type A Wire-Braid Armoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| BS 6883 Type A 3C × 2.5 mm² GSWB (UKOOA YD002) | 3 × 2.5 mm² | 2.5 mm² | 14.3 | 72 | 335 | 86 | Standard BS 6883 A configurations
| BS 6883 Type A 4C × 6.0 mm² GSWB (UKOOA YE004) | 4 × 6.0 mm² | 6.0 mm² | 19.2 | 230 | 640 | 115 | Standard BS 6883 A configurations
| BS 6883 Type A 4C × 16 mm² GSWB (UKOOA YE006) | 4 × 16 mm² | 16.0 mm² | 25 | 614 | 1240 | 150 | Standard BS 6883 A configurations
| BS 6883 Type A 4C × 35 mm² GSWB (UKOOA YE008) | 4 × 35 mm² | 35.0 mm² | 31.8 | 1344 | 2180 | 191 | Standard BS 6883 A configurations
| BS 6883 Type A 3C × 95 mm² GSWB (UKOOA YD011) | 3 × 95 mm² | 95.0 mm² | 42.6 | 2736 | 4120 | 256 | Standard BS 6883 A configurations
| BS 6883 Type A 1C × 240 mm² PBWB (UKOOA YA014) | 1 × 240 mm² (PBWB) | 240.0 mm² | 32 | 2580 | 3190 | 192 | Standard BS 6883 A configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per BS 6883 / UKOOA (Type A Wire-Braid Armoured 0.6/1 kV GP4 / SW4).

## Electrical & ampacity
BS 6883 A rmoured Offshore Power Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type A Wire-Braid Armoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
3 × 2.5 mm² | 7.56 | 29 | 26 | 0.36 | 16.5 | 3500
4 × 6.0 mm² | 3.11 | 49 | 44 | 0.86 | 6.8 | 3500
4 × 16 mm² | 1.16 | 92 | 83 | 2.29 | 2.5 | 3500
4 × 35 mm² | 0.529 | 152 | 137 | 5.01 | 1.15 | 3500
3 × 95 mm² | 0.195 | 280 | 252 | 13.59 | 0.43 | 3500
1 × 240 mm² (PBWB) | 0.0762 | 615 | 550 | 34.32 | 0.2 | 3500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per BS 6883 / UKOOA (Type A Wire-Braid Armoured 0.6/1 kV GP4 / SW4).

## Technical data
BS 6883 A rmoured Offshore Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type A Wire-Braid Armoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | BS 6883 Type A (UKOOA wire-braid armoured offshore)
Key data | Rated voltage | 0.6/1 kV AC (3.5 kV AC / 5 min dielectric test)
Key data | Braid armour | GSWB / PBWB (Galv. steel (multi) · Bronze (1C))
Key data | Insulation | Type GP4 EPR (90 °C cross-linked rubber BS 7655)
Key data | Inner / Outer | Type SW4 / SW2 (LSZH oil- & mud-resistant elastomer)
Key data | Class approvals | DNV / LR / ABS (IEC 60332-3-22 Cat A bunched flame)
Electrical | Rated voltage U0/U | 0.6/1 kV AC (600/1000 V)
Electrical | AC dielectric test voltage | 3,500 V AC for 5 minutes
Electrical | Max. conductor operating temp. | +90 °C continuous · +250 °C short-circuit
Electrical | Armour earth-fault capability | High-coverage GSWB / PBWB / TCWB per BS 6883
Thermal | Operating temperature range | -40 °C to +90 °C fixed installation
Thermal | Minimum installation temp. | -20 °C
Mechanical | Min. bending radius | 6 × overall diameter (D) per BS 6883
Mechanical | Armour wire diameter | 0.30 mm or 0.45 mm galvanized steel
Resistance | Bunched vertical flame test | BS EN 60332-3-22 Category A & BS EN 60332-1-2
Resistance | Zero halogen, low smoke & oil | BS EN 60754-1 (< 0.5 % HCl) · BS EN 61034-2
Standards | Primary specification | BS 6883 Type A · BS 7655-1.2 (GP4) · BS
Standards | Classification societies | DNV, Lloyd's Register (LR), ABS, BV
Identification | Core identification | 1C: Black · 2C: Brown/Blue · 3C
Identification | Outer sheath colour | Black (or Grey / Blue Ex-i)

## Construction
BS 6883 A rmoured Offshore Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type A Wire-Braid Armoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned annealed copper conductor | BS EN 60228 Class 2 stranded (or Class 5 flexible) tinned copper (1.5 to 630 mm²) | BS 6883 / BS EN 60228
2 | Type GP4 EPR rubber insulation (90 °C) | Cross-linked ethylene-propylene elastomer Type GP4 per BS 7655-1.2 | BS 6883
3 | Elastomeric inner bedding | Extruded halogen-free low-smoke elastomeric inner sheath providing circular gland seal | BS 6883 Clause 9
4 | Wire braid armour (GSWB / PBWB / TCWB) | Galvanized steel wire braid (multi-core) or non-magnetic phosphor-bronze / tinned-Cu | BS 6883 Clause 10
5 | Type SW4 outer sheath (LSZH) | Cross-linked low-smoke zero-halogen, oil-resistant elastomer Type SW4 per BS 7655-2.6 | BS 6883 / BS 7655-2.6
| BS 6883 Type A Multi-Core GSWB (2C, 3C, 4C to 37C × 1.5–185 mm²) | Galvanized steel wire-braid armoured power and control feeders with UKOOA code references.
| BS 6883 Type A Single-Core PBWB / TCWB (1C × 16 to 630 mm²) | Non-magnetic phosphor-bronze or tinned-copper wire-braid armoured single-core AC/DC feeders.

## Quality and supply
BS 6883 A rmoured Offshore Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type A Wire-Braid Armoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric & insulation resistance — 3,500 V AC for 5 min core-to-core & core-to-armour | 100 % of drums
Routine test | DC conductor resistance & braid armour check — BS EN 60228 Class 2/5 R20; BS 6883 Clause 10 braid coverage | 100 % of drums
Sample test | GP4 & SW4 hot-set, oil & tear resistance — BS 7655-1.2 & BS 7655-2.6 elastomeric tests | Per production batch
Type test | BS EN 60332-3-22 Cat A flame, smoke & HCl gas — Cat A bunched vertical burn; < 0.5 % HCl; ≥ 60 % light transmittance | Class society approval
Standard / approval | BS 6883 Type A
Standard / approval | UKOOA Code Compliant
Standard / approval | DNV / LR / ABS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BS 6883 TYPE A 0.6/1KV GSWB/PBWB
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP