## Request a quote
Request a quotation for BS 6883 Armoured MV
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for BS 6883 Armoured MV.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6883-armoured-offshore-mv-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6883 Armoured MV Offshore Power Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-mv-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / IEC 60092-354 (1.9/3.3 kV to 8.7/15 kV Offshore MV). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| BS 6883 1.9/3.3 kV 3C × 35 mm² GSWB | 3 × 35 mm² (3.3 kV) | 35.0 mm² | 31.8 | 1008 | 2290 | 254 | Standard BS 6883 Armoured MV configurations
| BS 6883 3.8/6.6 kV 3C × 50 mm² Cu-Scr GSWB | 3 × 50 mm² (6.6 kV) | 50.0 mm² | 41.2 | 1680 | 3480 | 330 | Standard BS 6883 Armoured MV configurations
| BS 6883 3.8/6.6 kV 3C × 95 mm² Cu-Scr GSWB | 3 × 95 mm² (6.6 kV) | 95.0 mm² | 49.4 | 3020 | 5240 | 395 | Standard BS 6883 Armoured MV configurations
| BS 6883 6.35/11 kV 3C × 120 mm² Cu-Scr GSWB | 3 × 120 mm² (11 kV) | 120.0 mm² | 56.5 | 3790 | 6620 | 452 | Standard BS 6883 Armoured MV configurations
| BS 6883 6.35/11 kV 1C × 240 mm² Cu-Scr PBWB | 1 × 240 mm² (11 kV PBWB) | 240.0 mm² | 38.6 | 2740 | 3780 | 309 | Standard BS 6883 Armoured MV configurations
| BS 6883 8.7/15 kV 1C × 300 mm² Cu-Scr PBWB | 1 × 300 mm² (15 kV PBWB) | 300.0 mm² | 44.2 | 3410 | 4650 | 354 | Standard BS 6883 Armoured MV configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per BS 6883 / IEC 60092-354 (1.9/3.3 kV to 8.7/15 kV Offshore MV).

## Electrical & ampacity
BS 6883 Armoured MV Offshore Power Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-mv-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / IEC 60092-354 (1.9/3.3 kV to 8.7/15 kV Offshore MV). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
3 × 35 mm² (3.3 kV) | 0.529 | 155 | 140 | 5.01 | 1.12 | 6500
3 × 50 mm² (6.6 kV) | 0.391 | 190 | 171 | 7.15 | 0.82 | 11000
3 × 95 mm² (6.6 kV) | 0.195 | 280 | 252 | 13.59 | 0.43 | 11000
3 × 120 mm² (11 kV) | 0.154 | 325 | 292 | 17.16 | 0.35 | 17000
1 × 240 mm² (11 kV PBWB) | 0.0762 | 620 | 555 | 34.32 | 0.2 | 17000
1 × 300 mm² (15 kV PBWB) | 0.0607 | 730 | 655 | 42.9 | 0.18 | 24000
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per BS 6883 / IEC 60092-354 (1.9/3.3 kV to 8.7/15 kV Offshore MV).

## Technical data
BS 6883 Armoured MV Offshore Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-mv-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / IEC 60092-354 (1.9/3.3 kV to 8.7/15 kV Offshore MV). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage classes | 3.3 kV to 15 kV (1.9/3.3, 3.8/6.6, 6.35/11, 8.7/15 kV)
Key data | HV insulation | Type GP5 HV-EPR (Triple-extruded w/ semi-con screens)
Key data | Metallic screen | Tinned Cu Tape (Individual phase earth fault screen)
Key data | Braid armour | GSWB / PBWB (Galv. steel (3C) · Bronze (1C))
Key data | Inner / Outer | Type SW4 LSZH (Halogen-free elastomer BS 7655-2.6)
Key data | Partial discharge | ≤ 5 pC @ 1.73 U0 (100 % routine VLF / AC PD tested)
Electrical | Rated voltage classes U0/U | 1.9/3.3 kV · 3.8/6.6 kV · 6.35/11 kV ·
Electrical | Routine AC test voltage (5 min) | 6.5 kV (3.3 kV) · 11 kV (6.6 kV) · 17 kV
Electrical | Partial discharge (PD) limit | ≤ 5 pC at 1.73 × U0 (3.8/6.6 kV to 8.7/15 kV)
Electrical | Max. conductor operating temp. | +90 °C continuous · +250 °C short-circuit
Electrical | Impulse withstand (BIL) | 40 kV (3.3 kV) · 60 kV (6.6 kV) · 75/95 kV
Thermal | Operating temperature range | -40 °C to +90 °C fixed installation
Thermal | Minimum installation temp. | -20 °C
Mechanical | Min. bending radius | 8 × D (3-core) · 10 × D (1-core MV) per BS
Mechanical | Armour wire diameter | 0.30 mm or 0.45 mm GSWB / PBWB per BS 6883
Resistance | Bunched vertical flame test | BS EN 60332-3-22 Category A & BS EN 60332-1-2
Resistance | Zero halogen, low smoke & oil | BS EN 60754-1 (< 0.5 % HCl) · BS EN 61034-2
Standards | Primary specification | BS 6883 · BS 7655-1.2 (GP5) · BS 7655-2.6
Standards | Classification societies | DNV, Lloyd's Register (LR), ABS, BV
Identification | Phase identification | Numbered tape or Brown, Black, Grey core
Identification | Outer sheath colour | Red (standard UKOOA HV identification) or

## Construction
BS 6883 Armoured MV Offshore Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-mv-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / IEC 60092-354 (1.9/3.3 kV to 8.7/15 kV Offshore MV). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Compacted tinned copper conductor | BS EN 60228 Class 2 circular compacted (or Class 5 flexible) tinned copper (16 to 630 mm²) | BS 6883 / BS EN 60228
2 | Triple-extruded Semi-Con + GP5 HV-EPR | Extruded semi-con conductor screen + 90 °C Type GP5 HV-EPR (BS 7655-1.2) + peelable | BS 6883 / BS 7655-1.2
3 | Tinned copper tape phase screen | Helically lapped annealed tinned copper tape (≥ 20 % overlap) over each core (3.8/6.6 kV | BS 6883 Clause 8
4 | Extruded SW4 inner bedding | Halogen-free low-smoke cross-linked elastomeric inner sheath | BS 6883 Clause 9
5 | Wire braid armour (GSWB / PBWB) | Galvanized steel wire braid (3-core) or non-magnetic phosphor-bronze wire braid (1-core) | BS 6883 Clause 10
6 | Type SW4 MV outer sheath | Cross-linked low-smoke zero-halogen oil-resistant elastomer Type SW4 (HV Red or Black) | BS 6883 / BS 7655-2.6
| 1.9/3.3 kV & 3.8/6.6 kV BS 6883 Armoured MV (1C & 3C) | Offshore medium-voltage motor and transformer feeders with GSWB (3C) or PBWB (1C) wire-braid armour.
| 6.35/11 kV & 8.7/15 kV BS 6883 Armoured MV (1C & 3C) | Primary offshore turbine-generator and ring-main MV cables with full copper tape screens and PD ≤ 5 pC.

## Quality and supply
BS 6883 Armoured MV Offshore Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-armoured-offshore-mv-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / IEC 60092-354 (1.9/3.3 kV to 8.7/15 kV Offshore MV). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Partial discharge (PD) test at 1.73 × U0 — ≤ 5 pC detectable discharge on 100 % of MV drums | 100 % of drums
Routine test | HV AC dielectric test (6.5 / 11 / 17 / 24 kV) — 5 minutes AC withstand without breakdown per BS 6883 | 100 % of drums
Sample test | Tan δ (dielectric loss angle) vs. voltage & temp. — BS 6883 / IEC 60502-2 Type GP5 HV-EPR verification | Per production batch
Type test | Lightning impulse (BIL) + 4 h 4×U0 voltage test — Pass full thermal cycle + impulse + BS EN 60332-3-22 Cat A | Class society approval
Standard / approval | BS 6883 (MV 3.3–15 kV)
Standard / approval | BS 7655-1.2 Type GP5
Standard / approval | DNV / LR / ABS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BS 6883 ARMOURED MV 3.3KV / 6.6KV
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP