## Request a quote
Request a quotation for BS 6883 UIS / UCS
Application engineer · offshore, FPSO & marine cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6883-unarmoured-individually-or-collectively-screened-offshore-instrumentation-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6883 UIS / UCS Unarmoured Offshore Instrumentation Cable – Dimensions, UKOOA codes & weights (18)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-individually-or-collectively-screened-offshore-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Codes GF & GH) / BS 7655 / IEC 60332-3-22. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation (UKOOA) | Format | Screen type | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| BS6883-UCS 1P×0.75 (GF107) | 1×2×0.75 mm² | UCS (OS) | 7.2 | 19 | 76 | 43 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UCS 1T×0.75 (GF132) | 1×3×0.75 mm² | UCS (OS) | 7.7 | 26 | 88 | 46 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UCS 2P×0.75 (GF108) | 2×2×0.75 mm² (Quad) | UCS (OS) | 8.6 | 34 | 112 | 52 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UCS 3P×0.75 (GF109) | 3×2×0.75 mm² | UCS (OS) | 11.4 | 48 | 172 | 68 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UCS 7P×0.75 (GF110) | 7×2×0.75 mm² | UCS (OS) | 14.8 | 108 | 305 | 89 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UCS 12P×0.75 (GF111) | 12×2×0.75 mm² | UCS (OS) | 19.2 | 182 | 495 | 115 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UCS 20P×0.75 (GF112) | 20×2×0.75 mm² | UCS (OS) | 23.8 | 302 | 768 | 143 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UIS 3P×0.75 (GH109) | 3×2×0.75 mm² | UIS (IS+OS) | 12.2 | 62 | 202 | 73 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UIS 7P×0.75 (GH110) | 7×2×0.75 mm² | UIS (IS+OS) | 16.2 | 140 | 365 | 97 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UIS 12P×0.75 (GH111) | 12×2×0.75 mm² | UIS (IS+OS) | 21 | 238 | 590 | 126 | 0.75 mm² (24/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 26.7 Ω/km (UKOOA GF/GH)
| BS6883-UCS 1P×1.0 (GF114) | 1×2×1.0 mm² | UCS (OS) | 7.6 | 24 | 86 | 46 | 1.0 mm² (32/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 20.0 Ω/km (UKOOA GF/GH)
| BS6883-UIS 3P×1.0 (GH116) | 3×2×1.0 mm² | UIS (IS+OS) | 13 | 78 | 236 | 78 | 1.0 mm² (32/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 20.0 Ω/km (UKOOA GF/GH)
| BS6883-UIS 7P×1.0 (GH117) | 7×2×1.0 mm² | UIS (IS+OS) | 17.2 | 178 | 428 | 103 | 1.0 mm² (32/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 20.0 Ω/km (UKOOA GF/GH)
| BS6883-UIS 12P×1.0 (GH118) | 12×2×1.0 mm² | UIS (IS+OS) | 22.4 | 302 | 695 | 134 | 1.0 mm² (32/0.20 mm) — L/R ≤ 25 µH/Ω · R₂₀ ≤ 20.0 Ω/km (UKOOA GF/GH)
| BS6883-UCS 1P×1.5 (GF121) | 1×2×1.5 mm² | UCS (OS) | 8.4 | 34 | 108 | 50 | 1.5 mm² (30/0.25 mm) — L/R ≤ 40 µH/Ω · R₂₀ ≤ 13.7 Ω/km (UKOOA GF/GH)
| BS6883-UIS 3P×1.5 (GH123) | 3×2×1.5 mm² | UIS (IS+OS) | 14.6 | 108 | 304 | 88 | 1.5 mm² (30/0.25 mm) — L/R ≤ 40 µH/Ω · R₂₀ ≤ 13.7 Ω/km (UKOOA GF/GH)
| BS6883-UIS 7P×1.5 (GH124) | 7×2×1.5 mm² | UIS (IS+OS) | 19.4 | 248 | 558 | 116 | 1.5 mm² (30/0.25 mm) — L/R ≤ 40 µH/Ω · R₂₀ ≤ 13.7 Ω/km (UKOOA GF/GH)
| BS6883-UCS 1P×2.5 (GF128) | 1×2×2.5 mm² | UCS (OS) | 9.8 | 53 | 148 | 59 | 2.5 mm² (50/0.25 mm) — L/R ≤ 60 µH/Ω · R₂₀ ≤ 8.21 Ω/km (UKOOA GF/GH)
UKOOA First Letter 'G' = Grey outer sheath (standard); replace 'G' with 'B' (e.g. BF107 / BH110) for Blue Ex-i outer sheath.

## Electrical parameters by cross-
BS 6883 UIS / UCS Unarmoured Offshore Instrumentation Cable – Electrical parameters by cross-section (Class 5 tinned copper) (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-individually-or-collectively-screened-offshore-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Codes GF & GH) / BS 7655 / IEC 60332-3-22. Values for your order are confirmed in the quotation.
Conductor size | Max. DC R @ 20 °C Ω/km | Max. L/R ratio µH/Ω | Max. C (UCS) nF/km | Max. C (UIS) nF/km
0.75 mm² (24/0.20 mm) | 26.7 | 25 | 200 | 250
1.00 mm² (32/0.20 mm) | 20 | 25 | 200 | 250
1.50 mm² (30/0.25 mm) | 13.7 | 40 | 200 | 250
2.50 mm² (50/0.25 mm) | 8.21 | 60 | 200 | 250
For fire-survival circuits requiring 950 °C for 3 hours, specify BS 7917 mica-glass taped UIS/UCS offshore cable.

## Technical data
BS 6883 UIS / UCS Unarmoured Offshore Instrumentation Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-individually-or-collectively-screened-offshore-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Codes GF & GH) / BS 7655 / IEC 60332-3-22. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 150/250 V (300 V class (600/1000 V option))
Key data | UKOOA types | UCS (GF) / UIS (UCS: Collective · UIS: Ind+Coll)
Key data | Insulation | EPR GP4 (+90 °C) (cross-linked elastomer BS 7655)
Key data | Outer sheath | SW4 LSZH (+90°C) (oil-resistant halogen-free)
Key data | Flame test | IEC 60332-3-22 (Category A bunched vertical)
Key data | Temperature | −40 °C to +90 °C (fixed arctic & tropical offshore)
Electrical | Voltage rating (U₀/U) | 150/250 V (300 V class) standard · 600/1000 V heavy-duty option
Electrical | Test voltage (core-to-core / screen) | 1500 V AC rms for 5 min (150/250 V grade) · 3500 V AC (600/1000 V grade)
Electrical | Max. conductor DC resistance @ 20 °C | 26.7 (0.75) · 20.0 (1.0) · 13.7 (1.5) · 8.21 Ω/km (2.5 mm² Cl.5)
Electrical | Max. mutual capacitance @ 1 kHz | ≤ 200 nF/km (UCS) · ≤ 250 nF/km (UIS)
Electrical | Max. L/R ratio (inductance / resistance) | ≤ 25 µH/Ω (0.75 & 1.0 mm²) · ≤ 40 µH/Ω (1.5 mm²) · ≤ 60 µH/Ω (2.5 mm²)
Thermal | Continuous conductor temperature | +90 °C (short-circuit rating +250 °C for 5 s)
Thermal | Ambient operating range | −40 °C to +90 °C (fixed) · −25 °C to +90 °C (installation)
Mechanical | Min. bending radius, fixed | 6 × OD (unarmoured UIS / UCS elastomeric construction)
Mechanical | Tear & abrasion resistance | Heavy-duty cross-linked SW4 thermoset rubber jacket
Resistance | Bunched vertical flame test | IEC 60332-3-22 Category A (7 litres/m non-metallic volume, 40 min burner)
Resistance | Halogen gas & smoke emission | IEC 60754-1 (HCl ≤ 0.5 %), IEC 60754-2 & IEC 61034-2 (≥ 60 % light)
Resistance | Oil & fluid immersion | BS 7655-2.6 Type SW4 mineral oil, diesel & chemical resistance at +100 °C
Standards | Design & offshore code standards | BS 6883, UKOOA (Codes GF & GH), BS 7655-1.2 (GP4) & BS 7655-2.6 (SW4)
Standards | Classification society type approvals | Lloyd's Register (LR), DNV & ABS offshore unit rules compatible
Identification | Core identification | Pairs: Bk/Wh numbered · Triads: Bk/Wh/Rd numbered · Quads: Bk/Wh/Rd/Bu
Identification | Outer sheath colour | Grey (standard non-Ex-i) or Blue (Ex-i intrinsic safety)
Identification | Customs tariff (HS) | 8544.49

## Construction
BS 6883 UIS / UCS Unarmoured Offshore Instrumentation Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-individually-or-collectively-screened-offshore-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Codes GF & GH) / BS 7655 / IEC 60332-3-22. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 flexible tinned annealed copper | 0.75 mm² (24/0.20 mm), 1.0 mm² (32/0.20 mm), 1.5 mm² (30/0.25 mm) or 2.5 mm² (50/0.25 mm) per BS EN 60228 (Class 2 optional)
2 | Cross-linked EPR elastomer (Type GP4) | Ethylene Propylene Rubber (GP4 to BS 7655-1.2) rated +90 °C continuous / +250 °C short-circuit
3 | Type UCS (Collective) or Type UIS (Individual + Collective) screen | Aluminium/PET tape (≥ 100 % coverage) in contact with 0.5 mm² tinned copper drain wire; pair screens isolated by PET tape on Type UIS
4 | Cross-linked oil-resistant LSZH elastomer (Type SW4) | Reduced-halogen / zero-halogen thermoset elastomeric compound (SW4 to BS 7655-2.6) in Grey or Blue (Ex-i)
| Type UCS (UKOOA Code GF — Collective Screen) | Unarmoured Collectively Screened pairs/triads with overall Al/PET foil + tinned copper drain wire
| Type UIS (UKOOA Code GH — Ind. + Coll. Screen) | Unarmoured Individually & Collectively Screened pairs/triads eliminating inter-pair crosstalk
| Ex-i Intrinsically Safe (Blue SW4 Sheath) | RAL 5015 Blue SW4 thermoset LSZH outer sheath for Zone 1 / Zone 2 Ex-i offshore loops

## Quality and supply
BS 6883 UIS / UCS Unarmoured Offshore Instrumentation Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-individually-or-collectively-screened-offshore-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Codes GF & GH) / BS 7655 / IEC 60332-3-22. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1500 V / 3500 V AC spark & 5-minute water-immersion voltage test — No breakdown during 5 min AC test in water bath per BS 6883 | Every manufactured drum
Sample test | IEC 60332-3-22 Cat A flame, IEC 60754-1/2 halogen & BS 7655 SW4 oil test — Char ≤ 2.5 m under Cat A 7 L/m flame; HCl ≤ 0.5 %; pass hot oil immersion | Periodic audit & type test
Standard / approval | BS 6883 & UKOOA (Codes GF/GH/BF/BH) Compliant
Standard / approval | IEC 60332-3-22 Cat A, IEC 60754 & IEC 61034
Standard / approval | BS 7655-1.2 (GP4) & BS 7655-2.6 (SW4)
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BS 6883 <UIS/UCS> <size> 150/250V UKOOA <code > SW4 IEC 60332-3-22 CAT A CE
Supply | Delivery form: Non-returnable fumigated wooden drums
Supply | Standard lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP