## Request a quote
Request a quotation for BS 6883 U
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for BS 6883 U.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-6883-unarmoured-offshore-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 6883 U narmoured Offshore Power Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type U Unarmoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| BS 6883 Type U 3C × 2.5 mm² GP4/SW4 | 3 × 2.5 mm² | 2.5 mm² | 10.6 | 72 | 165 | 64 | Standard BS 6883 U configurations
| BS 6883 Type U 4C × 6.0 mm² GP4/SW4 | 4 × 6.0 mm² | 6.0 mm² | 15.1 | 230 | 395 | 91 | Standard BS 6883 U configurations
| BS 6883 Type U 4C × 16 mm² GP4/SW4 | 4 × 16 mm² | 16.0 mm² | 20.6 | 614 | 875 | 124 | Standard BS 6883 U configurations
| BS 6883 Type U 1C × 70 mm² GP4/SW4 | 1 × 70 mm² | 70.0 mm² | 16.2 | 672 | 810 | 97 | Standard BS 6883 U configurations
| BS 6883 Type U 1C × 185 mm² GP4/SW4 | 1 × 185 mm² | 185.0 mm² | 24.4 | 1776 | 2040 | 146 | Standard BS 6883 U configurations
| BS 6883 Type U 1C × 300 mm² GP4/SW4 | 1 × 300 mm² | 300.0 mm² | 30.2 | 2880 | 3240 | 181 | Standard BS 6883 U configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per BS 6883 / UKOOA (Type U Unarmoured 0.6/1 kV GP4 / SW4).

## Electrical & ampacity
BS 6883 U narmoured Offshore Power Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type U Unarmoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
3 × 2.5 mm² | 7.56 | 30 | 27 | 0.36 | 16.5 | 3500
4 × 6.0 mm² | 3.11 | 50 | 45 | 0.86 | 6.8 | 3500
4 × 16 mm² | 1.16 | 94 | 84 | 2.29 | 2.5 | 3500
1 × 70 mm² | 0.27 | 285 | 255 | 10.01 | 0.54 | 3500
1 × 185 mm² | 0.1 | 530 | 475 | 26.46 | 0.24 | 3500
1 × 300 mm² | 0.0607 | 735 | 660 | 42.9 | 0.18 | 3500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per BS 6883 / UKOOA (Type U Unarmoured 0.6/1 kV GP4 / SW4).

## Technical data
BS 6883 U narmoured Offshore Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type U Unarmoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | BS 6883 Type U (UKOOA unarmoured offshore power)
Key data | Rated voltage | 0.6/1 kV AC (3.5 kV AC / 5 min dielectric test)
Key data | Conductor | Class 2 / 5 SnCu (Tinned annealed copper BS EN 60228)
Key data | Insulation | Type GP4 EPR (90 °C elastomeric BS 7655-1.2)
Key data | Outer sheath | Type SW4 EVA/LS (Low-smoke zero-halogen BS 7655-2.6)
Key data | Flame test | IEC 60332-3-22 (Category A bunched vertical flame)
Electrical | Rated voltage U0/U | 0.6/1 kV AC (600/1000 V)
Electrical | AC dielectric test voltage | 3,500 V AC for 5 minutes
Electrical | Max. conductor operating temp. | +90 °C continuous · +250 °C short-circuit
Electrical | Insulation resistance constant Ki | ≥ 3.67 MΩ·km at +90 °C per BS 6883
Thermal | Operating temperature range | -40 °C to +90 °C (fixed installation)
Thermal | Minimum installation temp. | -20 °C
Mechanical | Min. bending radius | 4 × D (D ≤ 10 mm) · 6 × D (D > 10 mm) per
Mechanical | Tear & abrasion resistance | Cross-linked thermoset Type SW4 elastomer
Resistance | Bunched vertical flame test | BS EN 60332-3-22 Category A & BS EN 60332-1-2
Resistance | Zero halogen, low smoke & oil | BS EN 60754-1 (< 0.5 % HCl) · BS EN 61034-2
Standards | Primary specification | BS 6883 · BS 7655-1.2 (GP4) · BS 7655-2.6
Standards | Classification societies | DNV, Lloyd's Register (LR), ABS, BV
Identification | Core identification | 1C: Black or G/Y · 2C: Brown/Blue · 3C
Identification | Outer sheath colour | Black (Grey or Blue Ex-i on request)

## Construction
BS 6883 U narmoured Offshore Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type U Unarmoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned annealed copper conductor | BS EN 60228 Class 2 circular stranded (or Class 5 flexible) tinned copper (1.5 to 630 mm²) | BS 6883 / BS EN 60228
2 | Type GP4 EPR rubber insulation (90 °C) | Cross-linked ethylene-propylene elastomer Type GP4 per BS 7655-1.2 | BS 6883 / BS 7655-1.2
3 | Halogen-free binder / filler | Low-smoke zero-halogen core bedding and polyester binder tape | BS 6883
4 | Type SW4 elastomeric outer sheath | Cross-linked halogen-free, low-smoke, oil-resistant elastomer Type SW4 per BS 7655-2.6 | BS 6883 / BS 7655-2.6
| BS 6883 Type U Single-Core (1C × 10 to 630 mm²) | Unarmoured single-core GP4/SW4 feeder for LV switchboards, generator tails, and earthing (Green/Yellow).
| BS 6883 Type U Multi-Core (2C, 3C, 4C, 5C to 37C × 1.5–95 mm²) | Unarmoured power, lighting, and control cables with UKOOA code designations.

## Quality and supply
BS 6883 U narmoured Offshore Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-6883-unarmoured-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6883 / UKOOA (Type U Unarmoured 0.6/1 kV GP4 / SW4). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric & insulation resistance — 3,500 V AC for 5 min per BS 6883; Ki ≥ 3.67 MΩ·km @ 90 °C | 100 % of drums
Routine test | DC conductor resistance @ 20 °C — BS EN 60228 Class 2 / Class 5 tinned copper limits | 100 % of drums
Sample test | GP4 & SW4 hot-set, oil immersion & tear tests — BS 7655-1.2 & BS 7655-2.6 elastomeric qualification | Per production batch
Type test | BS EN 60332-3-22 Cat A flame, smoke & HCl gas — Cat A vertical tray burn; < 0.5 % HCl; ≥ 60 % light transmittance | Class society approval
Standard / approval | BS 6883 Type U
Standard / approval | UKOOA Code Compliant
Standard / approval | DNV / LR / ABS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BS 6883 TYPE U 0.6/1KV GP4/SW4
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP