## Request a quote
Request a quotation for BS 7629-1
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-7629-1-screened-fire-resistant-alarm-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 7629-1 Screened Fire-Resistant Alarm Cable – Dimensions & masses (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7629-1-screened-fire-resistant-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7629-1 / BS 5839-1. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores × mm² | Cross-section | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| BS 7629-1 Std 2×1.0+E | 2×1.0 + 1.0 CPC | 1.0 mm² | 7.4 | 29 | 78 | 44 | BS 7629-1 standard series
| BS 7629-1 Std 2×1.5+E | 2×1.5 + 1.5 CPC | 1.5 mm² | 8 | 43 | 95 | 48 | BS 7629-1 standard series
| BS 7629-1 Std 2×2.5+E | 2×2.5 + 2.5 CPC | 2.5 mm² | 9.4 | 72 | 138 | 56 | BS 7629-1 standard series
| BS 7629-1 Std 2×4.0+E | 2×4.0 + 4.0 CPC | 4.0 mm² | 11.2 | 115 | 198 | 67 | BS 7629-1 standard series
| BS 7629-1 Std 3×1.5+E | 3×1.5 + 1.5 CPC | 1.5 mm² | 8.6 | 58 | 116 | 52 | BS 7629-1 standard series
| BS 7629-1 Std 3×2.5+E | 3×2.5 + 2.5 CPC | 2.5 mm² | 10.1 | 96 | 168 | 61 | BS 7629-1 standard series
| BS 7629-1 Std 4×1.5+E | 4×1.5 + 1.5 CPC | 1.5 mm² | 9.5 | 72 | 140 | 57 | BS 7629-1 standard series
| BS 7629-1 Std 4×2.5+E | 4×2.5 + 2.5 CPC | 2.5 mm² | 11.2 | 120 | 205 | 67 | BS 7629-1 standard series
| BS 7629-1 Std 7×1.5+E | 7×1.5 + 1.5 CPC | 1.5 mm² | 11.6 | 115 | 215 | 70 | BS 7629-1 standard series
| BS 7629-1 Enh 2×1.5+E | 2×1.5 + 1.5 CPC (Enh) | 1.5 mm² | 8.5 | 43 | 108 | 51 | BS 7629-1 standard series
| BS 7629-1 Enh 2×2.5+E | 2×2.5 + 2.5 CPC (Enh) | 2.5 mm² | 9.9 | 72 | 152 | 59 | BS 7629-1 standard series
| BS 7629-1 Enh 4×1.5+E | 4×1.5 + 1.5 CPC (Enh) | 1.5 mm² | 10.1 | 72 | 158 | 61 | BS 7629-1 standard series
| BS 7629-1 Enh 4×2.5+E | 4×2.5 + 2.5 CPC (Enh) | 2.5 mm² | 11.8 | 120 | 224 | 71 | BS 7629-1 standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per BS 7629-1 / BS 5839-1.

## Electrical data
BS 7629-1 Screened Fire-Resistant Alarm Cable – Electrical data (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7629-1-screened-fire-resistant-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7629-1 / BS 5839-1. Values for your order are confirmed in the quotation.
Cores × mm² | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
2×1.0 + 1.0 CPC | 18.1 | 15 | 13
2×1.5 + 1.5 CPC | 12.1 | 19 | 16
2×2.5 + 2.5 CPC | 7.41 | 26 | 22
2×4.0 + 4.0 CPC | 4.61 | 34 | 29
3×1.5 + 1.5 CPC | 12.1 | 17 | 15
3×2.5 + 2.5 CPC | 7.41 | 23 | 20
4×1.5 + 1.5 CPC | 12.1 | 17 | 15
4×2.5 + 2.5 CPC | 7.41 | 23 | 20
7×1.5 + 1.5 CPC | 12.1 | 13 | 11
2×1.5 + 1.5 CPC (Enh) | 12.1 | 19 | 16
2×2.5 + 2.5 CPC (Enh) | 7.41 | 26 | 22
4×1.5 + 1.5 CPC (Enh) | 12.1 | 17 | 15
4×2.5 + 2.5 CPC (Enh) | 7.41 | 23 | 20
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
BS 7629-1 Screened Fire-Resistant Alarm Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7629-1-screened-fire-resistant-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7629-1 / BS 5839-1. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (Fire alarm, voice evac & lighting)
Key data | Fire categories | Std 30 / Enh 120 (BS 8434-1 (30m) & BS 8434-2 (120m))
Key data | Screen & CPC | Al-PET + Cu CPC (Bonded Al tape + full-size tinned Cu)
Key data | Insulation | EI5 / Mica + EI5 (Ceramifying silicone / mica-polymer)
Key data | Operating temp | -20 to +70 °C (Fixed installation (min. 0 °C bend))
Key data | Min. bend radius | 6 × cable OD (Easy-form dressable Al screen)
Electrical | Rated voltage U0/U | 300/500 V
Electrical | Routine AC test voltage | 2.0 kV rms for 5 minutes
Electrical | Mutual capacitance @ 1 kHz | ≈95 pF/m (1.5 mm² 2-core)
Thermal | Operating temperature range | -20 °C to +70 °C
Thermal | Max. short-circuit temperature | +250 °C
Thermal | Recommended installation temp. | 0 °C to +60 °C
Mechanical | Minimum internal bend radius | 6 × overall cable diameter
Mechanical | CPC conductor size | Equal to phase cross-section (1.0–4.0 mm²)
Resistance | Standard 30 fire test | BS EN 50200 PH30/PH60 + BS 8434-1 (30 min flame/impact/water) + BS 6387 CWZ
Resistance | Enhanced 120 fire test | BS EN 50200 PH120 + BS 8434-2 (930 °C, 60 min flame+shock + 60 min flame+shock+water)
Resistance | Halogen acid gas & smoke | BS EN 60754-1 (<0.5 % HCl) & BS EN 61034-2 (>60 % light transmittance)
Standards | Cable manufacture | BS 7629-1
Standards | System design codes | BS 5839-1, BS 5839-8, BS 5839-9 & BS 5266-1
Identification | Core colours | 2-core: Brown, Blue · 3-core: Brown, Black, Grey · 4-core: Blue, Brown, Black, Grey
Identification | Sheath colours | Red (fire alarm) or White (emergency lighting)

## Construction
BS 7629-1 Screened Fire-Resistant Alarm Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7629-1-screened-fire-resistant-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7629-1 / BS 5839-1. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Plain annealed copper | Solid Class 1 (1.0–2.5 mm²) or stranded Class 2 (4.0 mm²) copper per BS EN 60228 | BS EN 60228
2 | Mica-glass fire barrier (Enhanced) | Glass-mica tape applied under insulation on Enhanced 120 grade for 930 °C impact + water survival | BS 8434-2
3 | Fire-resistant thermoset insulation | Cross-linked mineral-ceramic silicone / damage-resistant EI5 compound per BS 7655-1.5 | BS 7655-1.5
4 | Full-size circuit protective conductor | Uninsulated tinned annealed copper earth conductor matching phase cross-section, laid in direct contact with screen | BS 7629-1
5 | Bonded aluminium/copolymer tape | Longitudinal aluminium/PET tape bonded to outer sheath for automatic stripping and 100 % electrostatic screening | BS 7629-1
6 | LTS3 LSZH outer sheath | Thermoplastic low-smoke zero-halogen compound type LTS3 per BS 7655-6.1 (Red for fire alarm, White for emergency lighting) | BS 7655-6.1
| BS 7629-1 Standard 30 (PH30) | Meets BS 5839-1 Standard grade: BS EN 50200 PH30 & PH60 (842 °C with shock), BS 8434-1 (30 min fire + impact + water) and BS 6387 CWZ.
| BS 7629-1 Enhanced 120 (PH120) | Meets BS 5839-1 Enhanced grade: BS EN 50200 PH120 (120 min) and BS 8434-2 (120 min at 930 °C flame + impact + water spray) for multi-story phased evacuation.

## Quality and supply
BS 7629-1 Screened Fire-Resistant Alarm Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7629-1-screened-fire-resistant-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7629-1 / BS 5839-1. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 2.0 kV AC dielectric & spark test — No breakdown at 2.0 kV rms for 5 minutes | 100 % of reels/drums
Type test | BS EN 50200 PH30 / PH60 / PH120 fire with shock — Circuit survival under 842 °C flame and 5-minute hammer blows | LPCB / BASEC qualification
Type test | BS 8434-1 (30 min) & BS 8434-2 (120 min) fire + impact + water — Survival at 842 °C / 930 °C with direct impact and water spray | Standard & Enhanced qualification
Standard / approval | BS 7629-1
Standard / approval | BS 5839-1 Standard & Enhanced
Standard / approval | BS EN 50200 PH30 / PH60 / PH120
Standard / approval | BS 8434-1 & BS 8434-2
Standard / approval | BS 6387 CWZ
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BS 7629-1 ENHANCED 120 2x1.5mm2+E 300/500V BS EN 50200 PH120 BS 8434-2 LSZH [year]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP