## Request a quote
Request a quotation for BS 7917 A FR
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 7917 A FR Armoured Fire-Resistant Offshore Power Cable – Dimensions & masses (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7917 / IEC 60331-21. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores × mm² | Cross-section | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| BS 7917 A FR 2×2.5 GSWB (WM203) | 2×2.5 | 2.5 mm² | 14.8 | 49 | 340 | 118 | BS 7917 A FR standard series
| BS 7917 A FR 3×1.5 GSWB (WM302) | 3×1.5 | 1.5 mm² | 14.3 | 44 | 315 | 114 | BS 7917 A FR standard series
| BS 7917 A FR 3×2.5 GSWB (WM303) | 3×2.5 | 2.5 mm² | 15.5 | 74 | 385 | 124 | BS 7917 A FR standard series
| BS 7917 A FR 3×4 GSWB (WM304) | 3×4 | 4.0 mm² | 17.2 | 118 | 485 | 138 | BS 7917 A FR standard series
| BS 7917 A FR 3×6 GSWB (WM305) | 3×6 | 6.0 mm² | 18.6 | 176 | 595 | 149 | BS 7917 A FR standard series
| BS 7917 A FR 3×10 GSWB (WM306) | 3×10 | 10 mm² | 21.8 | 294 | 830 | 174 | BS 7917 A FR standard series
| BS 7917 A FR 3×16 GSWB (WM307) | 3×16 | 16 mm² | 24.4 | 470 | 1110 | 195 | BS 7917 A FR standard series
| BS 7917 A FR 3×25 GSWB (WM308) | 3×25 | 25 mm² | 28.5 | 735 | 1580 | 228 | BS 7917 A FR standard series
| BS 7917 A FR 3×35 GSWB (WM309) | 3×35 | 35 mm² | 31.2 | 1029 | 1960 | 250 | BS 7917 A FR standard series
| BS 7917 A FR 4×2.5 GSWB (WM403) | 4×2.5 | 2.5 mm² | 16.6 | 98 | 440 | 133 | BS 7917 A FR standard series
| BS 7917 A FR 4×6 GSWB (WM405) | 4×6 | 6.0 mm² | 20.2 | 235 | 705 | 162 | BS 7917 A FR standard series
| BS 7917 A FR 4×16 GSWB (WM407) | 4×16 | 16 mm² | 26.8 | 627 | 1360 | 214 | BS 7917 A FR standard series
| BS 7917 A FR 4×35 GSWB (WM409) | 4×35 | 35 mm² | 34.4 | 1372 | 2450 | 275 | BS 7917 A FR standard series
| BS 7917 A FR 1×185 PBWB (WM114) | 1×185 | 185 mm² | 30.2 | 1810 | 2490 | 242 | BS 7917 A FR standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per BS 7917 / IEC 60331-21.

## Electrical data
BS 7917 A FR Armoured Fire-Resistant Offshore Power Cable – Electrical data (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7917 / IEC 60331-21. Values for your order are confirmed in the quotation.
Cores × mm² | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
2×2.5 | 7.56 | 31 | 27
3×1.5 | 12.2 | 19 | 16
3×2.5 | 7.56 | 26 | 22
3×4 | 4.7 | 35 | 30
3×6 | 3.11 | 45 | 39
3×10 | 1.84 | 63 | 54
3×16 | 1.16 | 84 | 72
3×25 | 0.734 | 110 | 95
3×35 | 0.529 | 137 | 118
4×2.5 | 7.56 | 26 | 22
4×6 | 3.11 | 45 | 39
4×16 | 1.16 | 84 | 72
4×35 | 0.529 | 137 | 118
1×185 | 0.1 | 435 | 374
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
BS 7917 A FR Armoured Fire-Resistant Offshore Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7917 / IEC 60331-21. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 600/1000 V (Also 150/250 V & 1.9/3.3 kV grades)
Key data | Fire integrity | IEC 60331-21 (180 min @ 750 °C circuit survival)
Key data | Braid armour | GSWB / PBWB (Galvanized steel or bronze wire braid)
Key data | Insulation | Mica + GP4 EPR (90 °C thermoset elastomer + mica)
Key data | Sheath compound | SW4 / SW2 LSZH (Inner bedding + outer oil/mud sheath)
Key data | Min. bend radius | 6×D / 8×D (6×OD (≤25 mm) · 8×OD (>25 mm))
Electrical | Rated voltage U0/U | 600/1000 V
Electrical | Routine AC test voltage | 3.5 kV rms for 5 minutes
Electrical | Braid transfer impedance | Provides mechanical armour + 360° EMC screening
Thermal | Continuous conductor temp. | +90 °C
Thermal | Max. short-circuit temp. | +250 °C (5 s)
Thermal | Operating temperature range | -40 °C to +90 °C
Mechanical | Min. bend radius (OD ≤25 mm) | 6 × overall cable diameter
Mechanical | Min. bend radius (OD >25 mm) | 8 × overall cable diameter
Resistance | Circuit integrity in fire | IEC 60331-21 (750 °C for 180 min) / IEC 60331-1
Resistance | Flame propagation | IEC 60332-3-22 Category A bunched vertical flame test
Resistance | Oil & drilling fluid resistance | BS 7655-2.6 SW4 / SW2 & NEK 606 mud immersion option
Standards | Design & test standard | BS 7917 & UKOOA Code of Practice
Standards | Marine classification | Lloyds Register, DNV, ABS type-approval ready
Identification | UKOOA type code | Type 'WM' (600/1000 V fire-resistant EPR/SW4/GSWB/SW4)
Identification | Outer sheath colour | Orange (RAL 2003) or Black

## Construction
BS 7917 A FR Armoured Fire-Resistant Offshore Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7917 / IEC 60331-21. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned annealed copper | Stranded circular tinned copper conductor, Class 2 per BS EN 60228 | BS EN 60228
2 | Mica-glass fire barrier | Helically applied phlogopite mica-glass tape over conductor | IEC 60331-21
3 | GP4 EPR thermoset insulation | Ethylene propylene rubber (EPR) compound type GP4 per BS 7655-1.2 | BS 7655-1.2
4 | SW4 elastomeric inner bedding | Extruded halogen-free cross-linked elastomeric bedding compound | BS 7655-2.6
5 | Wire braid armour (GSWB / PBWB) | Galvanized steel wire braid (multi-core) or non-magnetic phosphor-bronze wire braid (single-core) | BS 7917
6 | SW4 / SW2 offshore outer sheath | Heavy-duty cross-linked LSZH oil- and mud-resistant elastomer per BS 7655-2.6 (Orange or Black) | BS 7655-2.6
| BS 7917 A FR (GSWB Multi-Core) | Galvanized steel wire braid armour with SW4 or NEK 606 mud-resistant SW2 outer sheath for 2- to 37-core cables.
| BS 7917 A FR (PBWB Single-Core) | Non-magnetic phosphor-bronze wire braid armour for high-current single-core AC emergency generator feeders (50–630 mm²).

## Quality and supply
BS 7917 A FR Armoured Fire-Resistant Offshore Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7917 / IEC 60331-21. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric withstand test — 5 minutes between cores and wire braid armour | 100 % of drums
Type test | IEC 60331-21 / IEC 60331-1 fire integrity — 180 minutes @ ≥750 °C (plus mechanical shock option) | Type qualification
Type test | IEC 60332-3-22 Cat. A vertical flame & oil immersion — Passes Category A bunched burn and IRM 902/903 hot oil immersion | Type qualification
Standard / approval | BS 7917
Standard / approval | UKOOA Type WM / WJ
Standard / approval | IEC 60331-21 (750 °C, 3 h)
Standard / approval | IEC 60332-3-22 Cat. A
Standard / approval | BS 7655-2.6 SW4 / SW2
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BS 7917 600/1000V FIRE RESISTANT 3x16mm2 GP4/SW4/GSWB/SW4 UKOOA WM307 IEC 60331-21 [year]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP