## Request a quote
Request a quotation for BS 7917 AIS FR / ACS FR
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-instrumentation-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS 7917 AIS FR / ACS FR Armoured Offshore Instrumentation Cable – Dimensions & UKOOA weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7917 / IEC 60331-21 / UKOOA. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | UKOOA code & pairs | Outer Ø ≈ mm | Weight ≈ kg/km | Max. DC R Ω/km | Min. bend R mm | Series
| BS 7917 ACS FR 1P×1.0 | FJK01 · 1 Pair 1.0 mm² | 11.6 | 215 | 18.2 | 93 | BS 7917 ACS FR — Collectively Screened
| BS 7917 ACS FR 2P×1.0 | FJK02 · 2 Pair 1.0 mm² | 15.2 | 345 | 18.2 | 122 | BS 7917 ACS FR — Collectively Screened
| BS 7917 ACS FR 5P×1.5 | FJL05 · 5 Pair 1.5 mm² | 21.8 | 730 | 12.2 | 174 | BS 7917 ACS FR — Collectively Screened
| BS 7917 AIS FR 2P×1.0 | FJQ02 · 2 Pair 1.0 mm² | 16 | 385 | 18.2 | 128 | BS 7917 AIS FR — Individually & Collectively Screened
| BS 7917 AIS FR 5P×1.0 | FJQ05 · 5 Pair 1.0 mm² | 21.4 | 685 | 18.2 | 171 | BS 7917 AIS FR — Individually & Collectively Screened
| BS 7917 AIS FR 10P×1.5 | FJR10 · 10 Pair 1.5 mm² | 29.2 | 1290 | 12.2 | 234 | BS 7917 AIS FR — Individually & Collectively Screened
Mica-glass tape slightly increases core diameter compared to BS 6883; verify gland inner sealing ring range against BS 7917 tables.

## Technical data
BS 7917 AIS FR / ACS FR Armoured Offshore Instrumentation Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7917 / IEC 60331-21 / UKOOA. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | BS 7917:1999 (Fire-resistant UKOOA offshore)
Key data | Fire survival | 180 min @ 750 °C (IEC 60331-21 & BS 6387 CWZ)
Key data | Voltage rating | 150/250 V (600/1000 V option available)
Key data | Fire barrier | Mica + GP4 EPR (Phlogopite glass-mica + EPR)
Key data | Armour & sheath | GSWB + SW4 LSZH (Galvanized steel braid + SW4)
Key data | Temperature | -40 to +90 °C (Continuous fixed service)
Electrical | Rated voltage (Uo/U) | 150/250 V (instrumentation) · 600/1000 V (control)
Electrical | Max. DC resistance @ 20 °C | 24.8 Ω/km (0.75) · 18.2 Ω/km (1.0) · 12.2 Ω/km (1.5) · 7.56 Ω/km (2.5)
Electrical | Mutual capacitance | ≤ 120 pF/m (ACS FR) · ≤ 150 pF/m (AIS FR)
Electrical | L/R ratio | ≤ 25 µH/Ω (0.75–1.0 mm²) · ≤ 40 µH/Ω (1.5 mm²)
Thermal | Operating temperature | -40 °C to +90 °C
Thermal | Fire survival rating | +750 °C for 180 min (IEC 60331-21) & +950 °C (BS 6387 Cat C)
Thermal | Short-circuit temperature | +250 °C (5 s)
Mechanical | Min. bend radius | 8 × OD (fixed installation)
Mechanical | Fire with mechanical shock | BS 6387 Category Z (+950 °C + 15 s hammer blows) & EN 50200
Mechanical | Fire with water spray | BS 6387 Category W (+650 °C + 15 min water sprinkler)
Resistance | Circuit integrity in fire | IEC 60331-21 / IEC 60331-31 & BS 6387 CWZ
Resistance | Bunched flame & LSZH | IEC 60332-3-22 Cat A, IEC 60754-1 & IEC 61034-2
Resistance | Oil & drilling fluid | BS 7655-2.6 Type SW4 hot oil & fuel resistant
Standards | Primary design standard | BS 7917 & UKOOA Fire-Resistant Code
Standards | Fire test standards | IEC 60331-21, BS 6387 CWZ & IEC 60332-3-22
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Core identification | Pairs: Black & White numbered · Triads: Black, White & Red
Identification | Outer sheath colour | Grey, Light Blue (Ex i), or Red/Orange (Fire & ESD)
Identification | Customs tariff (HS) | 8544.4993

## Construction
BS 7917 AIS FR / ACS FR Armoured Offshore Instrumentation Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7917 / IEC 60331-21 / UKOOA. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned annealed copper conductors | Class 2 stranded (7-wire) or Class 5 flexible tinned copper per BS EN 60228 (0.75, 1.0, 1.5, 2.5 mm²) | Maintains conductivity under +950 °C flame test
2 | Phlogopite mica-glass fire barrier | Overlapped helical wrap of silicone-bonded phlogopite mica-glass tape applied directly over each conductor
3 | GP4 / GP5 EPR thermoset insulation | Ethylene Propylene Rubber (EPR Type GP4 per BS 7655-1.2) extruded over the mica tape | 150/250 V or 600/1000 V primary dielectric
4 | Collective (ACS FR) or Individual + Collective (AIS FR) screen | Aluminium/PET tape with 0.50 mm² tinned copper drain wire | 100 % EMI screening for SIL-3 ESD & F&G signals
5 | SW4 bedding + Galvanized Steel Wire Braid (GSWB) | Halogen-free SW4 bedding + high-coverage galvanized steel wire braid armour
6 | SW4 Fire-Resistant Offshore Outer Sheath | Cross-linked LSZH oil/mud-resistant elastomer Type SW4 per BS 7655-2.6 (Grey, Blue Ex i, or Red F&G) | IEC 60332-3-22 Cat A & HCl < 0.5 %
| BS 7917 ACS FR (Collectively Screened) | Mica + EPR pairs/triads + overall Al/PET screen + GSWB armour + SW4 sheath (UKOOA F-codes)
| BS 7917 AIS FR (Individually & Collectively Screened) | Mica + EPR pairs/triads + individual & overall screens + GSWB armour + SW4 sheath

## Quality and supply
BS 7917 AIS FR / ACS FR Armoured Offshore Instrumentation Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bs-7917-armoured-fire-resistant-offshore-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 7917 / IEC 60331-21 / UKOOA. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1.5 kV / 3.5 kV AC dielectric & conductor resistance test — 5 min AC withstand without breakdown | Every drum length
Type test | IEC 60331-21 & BS 6387 CWZ fire-survival test — 3 h @ 750 °C + 950 °C flame, water spray (W) and shock (Z) without fuse failure | Type approval
Type test | IEC 60332-3-22 Cat A bunched flame & SW4 oil test — Pass Cat A vertical ladder burn and BS 7655-2.6 hot oil immersion | Type approval
Standard / approval | BS 7917 & UKOOA Fire-Resistant
Standard / approval | IEC 60331-21 & BS 6387 CWZ
Standard / approval | RoHS 2 & REACH Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BS 7917 UKOOA 150/250V AIS/ACS FR IEC 60331 GSWB SW4
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP