## Request a quote
Request a quotation for BS EN 60702-1
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mineral-insulated-metal-sheathed-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
BS EN 60702-1 Mineral-Insulated Metal-Sheathed Power Cable – Dimensions & masses (15)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-metal-sheathed-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 60702-1 / IEC 60702-1. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores × mm² | Cross-section | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| 2L1.5 (500 V Light Duty) | 2×1.5 | 1.5 mm² | 7.2 | 65 | 118 | 43 | BS EN 60702-1 standard series
| 2L2.5 (500 V Light Duty) | 2×2.5 | 2.5 mm² | 8.1 | 95 | 160 | 49 | BS EN 60702-1 standard series
| 3L1.5 (500 V Light Duty) | 3×1.5 | 1.5 mm² | 7.6 | 82 | 140 | 46 | BS EN 60702-1 standard series
| 4L1.5 (500 V Light Duty) | 4×1.5 | 1.5 mm² | 8.3 | 102 | 170 | 50 | BS EN 60702-1 standard series
| 4L2.5 (500 V Light Duty) | 4×2.5 | 2.5 mm² | 9.4 | 152 | 235 | 56 | BS EN 60702-1 standard series
| 2H2.5 (750 V Heavy Duty) | 2×2.5 | 2.5 mm² | 10.1 | 130 | 225 | 61 | BS EN 60702-1 standard series
| 4H4 (750 V Heavy Duty) | 4×4 | 4.0 mm² | 12.6 | 265 | 415 | 76 | BS EN 60702-1 standard series
| 4H6 (750 V Heavy Duty) | 4×6 | 6.0 mm² | 13.8 | 365 | 535 | 83 | BS EN 60702-1 standard series
| 4H10 (750 V Heavy Duty) | 4×10 | 10 mm² | 15.8 | 560 | 780 | 95 | BS EN 60702-1 standard series
| 4H16 (750 V Heavy Duty) | 4×16 | 16 mm² | 18 | 830 | 1110 | 108 | BS EN 60702-1 standard series
| 4H25 (750 V Heavy Duty) | 4×25 | 25 mm² | 21 | 1240 | 1620 | 126 | BS EN 60702-1 standard series
| 1H70 (750 V Heavy Duty) | 1×70 | 70 mm² | 14.8 | 860 | 1070 | 89 | BS EN 60702-1 standard series
| 1H120 (750 V Heavy Duty) | 1×120 | 120 mm² | 18.2 | 1410 | 1710 | 109 | BS EN 60702-1 standard series
| 1H185 (750 V Heavy Duty) | 1×185 | 185 mm² | 21.6 | 2120 | 2510 | 130 | BS EN 60702-1 standard series
| 1H240 (750 V Heavy Duty) | 1×240 | 240 mm² | 24.4 | 2720 | 3190 | 146 | BS EN 60702-1 standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per BS EN 60702-1 / IEC 60702-1.

## Electrical data
BS EN 60702-1 Mineral-Insulated Metal-Sheathed Power Cable – Electrical data (15)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-metal-sheathed-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 60702-1 / IEC 60702-1. Values for your order are confirmed in the quotation.
Cores × mm² | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
2×1.5 | 12.1 | 27 | 23
2×2.5 | 7.41 | 36 | 31
3×1.5 | 12.1 | 23 | 20
4×1.5 | 12.1 | 23 | 20
4×2.5 | 7.41 | 31 | 27
2×2.5 | 7.41 | 38 | 33
4×4 | 4.61 | 42 | 36
4×6 | 3.08 | 54 | 46
4×10 | 1.83 | 73 | 63
4×16 | 1.15 | 97 | 83
4×25 | 0.727 | 128 | 110
1×70 | 0.268 | 285 | 245
1×120 | 0.153 | 395 | 340
1×185 | 0.099 | 515 | 443
1×240 | 0.075 | 610 | 525
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
BS EN 60702-1 Mineral-Insulated Metal-Sheathed Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-metal-sheathed-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 60702-1 / IEC 60702-1. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 500 V / 750 V (Light duty 500 V · Heavy duty 750 V)
Key data | Fire survival | BS 6387 CWZ / F1 (Inorganic MgO (2800 °C) & Cu (1083 °C))
Key data | Insulation | Compressed MgO (Non-ageing inorganic magnesium oxide)
Key data | Metal sheath | Seamless Cu tube (Acts as armour + 100 % CPC earth path)
Key data | Bare Cu temp. | Up to +250 °C (Continuous bare sheath (+105 °C LSZH))
Key data | Min. bend radius | 6 × cable OD (Permanent formed bends)
Electrical | Rated voltage | 500 V (Light Duty) / 750 V (Heavy Duty)
Electrical | Routine AC test voltage | 1.5 kV (500 V grade) / 2.5 kV (750 V grade) for 1 min
Electrical | Insulation resistance @ 20 °C | ≥1000 MΩ·km (dry sealed termination)
Thermal | Bare copper sheath continuous temp. | Up to +250 °C (short-term up to +1000 °C)
Thermal | LSZH covered continuous temp. | -40 °C to +105 °C
Thermal | Copper / MgO melting points | Cu: 1083 °C · MgO: 2800 °C
Mechanical | Min. permanent bend radius | 6 × cable outer diameter
Mechanical | Radial crushing & impact | Withstands flattening to 50 % OD without short-circuit
Resistance | Fire, water & shock | BS 6387 Cat. C, W, Z & BS 8491 Cat. F120 (120 min)
Resistance | Reaction to fire (bare MICC) | Euroclass A1 non-combustible
Resistance | Water & gas ingress | 100 % impermeable seamless copper tube
Standards | Cable specification | BS EN 60702-1 / IEC 60702-1
Standards | Terminations specification | BS EN 60702-2 / IEC 60702-2 brass pot & gland seal
Identification | Core identification | Identified by continuity testing at brass pot termination and sleeved tails
Identification | Outer finish | Bare copper or LSZH orange / red / white

## Construction
BS EN 60702-1 Mineral-Insulated Metal-Sheathed Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-metal-sheathed-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 60702-1 / IEC 60702-1. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid copper conductor rods | High-conductivity annealed solid copper rods per BS EN 60702-1 | BS EN 60702-1
2 | Compacted MgO mineral | Highly compressed anhydrous magnesium oxide (MgO) powder (melting point 2800 °C) | BS EN 60702-1
3 | Seamless copper sheath | Seamless drawn phosphorus-deoxidized copper tube (melting point 1083 °C) providing gas/water tightness and CPC | BS EN 60702-1
4 | LSZH outer covering | Optional extruded zero-halogen polyolefin corrosion covering (orange or red) | BS EN 60702-1
| 500 V Light Duty (CC / LSF) | 2, 3, 4, 7, 12 and 19 cores from 1.0 to 2.5 mm² for fire alarm, emergency lighting and control circuits.
| 750 V Heavy Duty (HD / BTTZ) | 1, 2, 3 and 4 cores from 1.5 to 240 mm² for high-current life-safety sub-mains and firefighting risers.

## Quality and supply
BS EN 60702-1 Mineral-Insulated Metal-Sheathed Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-metal-sheathed-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 60702-1 / IEC 60702-1. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1.5 kV / 2.5 kV AC dielectric test & IR check — ≥1000 MΩ·km insulation resistance and zero breakdown | 100 % of coils/drums
Routine test | Seamless copper sheath pressure & integrity check — Eddy-current & dimensional verification of drawn Cu tube | 100 % of lengths
Type test | BS 6387 CWZ & BS 8491 F120 fire + impact + water — Full circuit continuity at 950 °C with shock and water spray | Type qualification
Standard / approval | BS EN 60702-1 / IEC 60702-1
Standard / approval | BS 6387 CWZ
Standard / approval | BS 8491 Cat. F120
Standard / approval | BS 5839-1 Enhanced & BS 8519 Cat. 3
Standard / approval | Euroclass A1 (bare Cu)
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX MICC BS EN 60702-1 750V 4H16 LSZH [year]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP