## Request a quote
Request a quotation for Battery Energy Storage DC Cable
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/battery-energy-storage-dc-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Battery Energy Storage DC Cable – Dimensions & masses (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/battery-energy-storage-dc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1973 / UL 9540A / EN 50618 / IEC 62930. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Metric (AWG/MCM) | Cond. Ø / Wall mm | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| BESS 1×16 mm² | 16 mm² (6 AWG) | 5.1 Ø · 1.5 mm | 8.2 | 153.6 | 195 | 32.8 | Battery Energy Storage DC Cable size schedule
| BESS 1×25 mm² | 25 mm² (4 AWG) | 6.3 Ø · 1.6 mm | 9.6 | 240 | 290 | 38.4 | Battery Energy Storage DC Cable size schedule
| BESS 1×35 mm² | 35 mm² (2 AWG) | 7.6 Ø · 1.6 mm | 10.9 | 336 | 395 | 43.6 | Battery Energy Storage DC Cable size schedule
| BESS 1×50 mm² | 50 mm² (1/0 AWG) | 9.1 Ø · 1.8 mm | 12.8 | 480 | 560 | 51.2 | Battery Energy Storage DC Cable size schedule
| BESS 1×70 mm² | 70 mm² (2/0 AWG) | 10.8 Ø · 1.8 mm | 14.5 | 672 | 765 | 58 | Battery Energy Storage DC Cable size schedule
| BESS 1×95 mm² | 95 mm² (3/0 AWG) | 12.5 Ø · 2.0 mm | 16.6 | 912 | 1025 | 66.4 | Battery Energy Storage DC Cable size schedule
| BESS 1×120 mm² | 120 mm² (4/0 AWG) | 14.2 Ø · 2.0 mm | 18.3 | 1152 | 1280 | 73.2 | Battery Energy Storage DC Cable size schedule
| BESS 1×150 mm² | 150 mm² (300 MCM) | 15.8 Ø · 2.2 mm | 20.3 | 1440 | 1590 | 81.2 | Battery Energy Storage DC Cable size schedule
| BESS 1×185 mm² | 185 mm² (350 MCM) | 17.5 Ø · 2.2 mm | 22 | 1776 | 1950 | 88 | Battery Energy Storage DC Cable size schedule
| BESS 1×240 mm² | 240 mm² (500 MCM) | 20.1 Ø · 2.4 mm | 25 | 2304 | 2510 | 100 | Battery Energy Storage DC Cable size schedule
| BESS 1×300 mm² | 300 mm² (600 MCM) | 22.5 Ø · 2.6 mm | 27.8 | 2880 | 3120 | 111.2 | Battery Energy Storage DC Cable size schedule
| BESS 1×400 mm² | 400 mm² (777 MCM) | 25.8 Ø · 2.8 mm | 31.5 | 3840 | 4130 | 126 | Battery Energy Storage DC Cable size schedule
Dimensions and tolerances conform to UL 1973 / UL 9540A / EN 50618 / IEC 62930.

## Electrical data
Battery Energy Storage DC Cable – Electrical data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/battery-energy-storage-dc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1973 / UL 9540A / EN 50618 / IEC 62930. Values for your order are confirmed in the quotation.
Metric (AWG/MCM) | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
16 mm² (6 AWG) | 1.24 | 135 | 108
25 mm² (4 AWG) | 0.795 | 180 | 144
35 mm² (2 AWG) | 0.565 | 225 | 180
50 mm² (1/0 AWG) | 0.393 | 285 | 228
70 mm² (2/0 AWG) | 0.277 | 355 | 284
95 mm² (3/0 AWG) | 0.21 | 430 | 344
120 mm² (4/0 AWG) | 0.164 | 500 | 400
150 mm² (300 MCM) | 0.132 | 575 | 460
185 mm² (350 MCM) | 0.108 | 655 | 524
240 mm² (500 MCM) | 0.082 | 775 | 620
300 mm² (600 MCM) | 0.065 | 895 | 716
400 mm² (777 MCM) | 0.05 | 1050 | 840
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
Battery Energy Storage DC Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/battery-energy-storage-dc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1973 / UL 9540A / EN 50618 / IEC 62930. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | DC voltage rating | 1500 V / 2000 V (1000 V / 1500 V AC rated)
Key data | Conductor | Class 5 / 6 tinn (IEC 60228 extra-flexible strands)
Key data | Insulation | E-beam cross-lin (Halogen-free LSZH thermoset (+125 °C))
Key data | Size range | 16 to 400 mm² (4 AWG to 777 MCM equivalents)
Key data | Operating temp | -40 to +120 / +1 (+250 °C short-circuit withstand)
Key data | Min. bend radius | 3 × to 4 × OD (Tight battery module bus turns)
Electrical | Rated voltage | 1,500 V DC (up to 1,800 / 2,000 V DC max) · 1,000 / 1,500 V AC
Electrical | Dielectric test voltage | 6.5 kV AC rms or 15 kV DC for 5 minutes
Electrical | Insulation resistance | ≥1,000 MΩ·km at +20 °C
Thermal | Continuous operating temperature | -40 °C to +120 / +125 °C
Thermal | Short-circuit temperature (5 s) | +250 °C thermoset cross-linked XLPO
Mechanical | Minimum bending radius | 3 × D (≤50 mm²) · 4 × D (>50 mm²) for compact battery rack turns
Mechanical | Conductor flexibility | IEC 60228 Class 5 (standard) or Class 6 (extra-fine 0.15/0.20 mm strands)
Resistance | Flame propagation & fire safety | UL 1581 VW-1, CSA FT1/FT4, IEC 60332-1-2 & IEC 60332-3-24 bunched flame
Resistance | Halogen, smoke & electrolyte resistance | IEC 60754-1/2 zero halogen, IEC 61034-2 low smoke; resists carbonate electrolyte & battery acid
Standards | Reference standards | UL 1973 / UL 9540A component compliance, TÜV 2 PfG 2693, BS EN 50618 & IEC 62930
Standards | North American dual rating | UL 3817 / UL 44 RHW-2 / UL 4703 PV / cULus 1500–2000 V options
Identification | Standard colours | Orange (RAL 2003), Black (RAL 9005), Red (RAL 3000), Blue
Identification | Surface legend | Printed with mm² & AWG size, 1500V/2000V DC, 125°C, VW-1, LSZH and metre marks

## Construction
Battery Energy Storage DC Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/battery-energy-storage-dc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1973 / UL 9540A / EN 50618 / IEC 62930. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 / Class 6 tinned copper (IEC 60228) | Extra-flexible rope-stranded tin-coated copper eliminating mechanical lever torque on battery module studs and plug-in connectors | IEC 60228
2 | Halogen-free separator tape | Applied on cross-sections ≥35 mm² for clean stripping on automated lug-crimping presses | EN 50618
3 | Cross-linked LSZH XLPO insulation/sheath | 125 °C electron-beam cross-linked halogen-free polyolefin (Orange RAL 2003, Black RAL 9005 or Red RAL 3000) meeting UL VW-1 / FT4 and IEC 60332-3 | EN 50618
| Orange RAL 2003 High-Voltage BESS Interconnect (16–120 mm²) | High-visibility orange 1500 V DC extra-flexible cable for battery module-to-module jumpers and HV rack harnesses with plug-in radlok connectors.
| Black & Red Polarity Feeder (95–400 mm²) | Heavy-section 1500/2000 V DC feeder cable connecting battery cluster combiner cabinets to PCS inverters.

## Quality and supply
Battery Energy Storage DC Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/battery-energy-storage-dc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1973 / UL 9540A / EN 50618 / IEC 62930. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 6.5 kV AC / 15 kV DC water-bath dielectric & spark test — Zero breakdown; resistance per IEC 60228 Class 5/6 | 100 % of drums
Sample test | Hot-set cross-linking, VW-1 vertical flame & -40 °C cold bend — Passes thermoset hot-set and vertical flame self-extinguish | Every batch
Type test | IEC 60332-3-24 bunched fire, smoke density & zero-halogen — Certified to TÜV 2 PfG 2693 / EN 50618 / UL 3817 | Type qualification
Standard / approval | TÜV 2 PfG 2693 / EN 50618 (1.5 kV DC)
Standard / approval | UL 3817 / UL 1973 Component
Standard / approval | UL VW-1 & CSA FT4 Flame
Standard / approval | IEC 60332-3-24 / EN 60754-1/2 LSZH
Standard / approval | RoHS 3 & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX BESS DC CABLE 1x[size]mm2 1500V/2000V DC 125C XLPO LSZH VW-1 FT4 [lot/m]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP