## Request a quote
Request a quotation for Bus Drop Cable
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/bus-drop-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Bus Drop Cable – Dimensions & masses (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bus-drop-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 / UL 62 / CSA C22.2 No. 49 / NEC Art. 368. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | 3 Phase + 3 Split Ground | Ground AWG / Amps | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| Bus Drop 14/3 | 3 × 14 AWG + 3G | 3×18 AWG Gd · 20 A | 9.4 | 68 | 138 | 56.4 | Bus Drop Cable size schedule
| Bus Drop 12/3 | 3 × 12 AWG + 3G | 3×16 AWG Gd · 25 A | 10.67 | 108 | 195 | 64 | Bus Drop Cable size schedule
| Bus Drop 10/3 | 3 × 10 AWG + 3G | 3×14 AWG Gd · 35 A | 12.19 | 172 | 285 | 73.1 | Bus Drop Cable size schedule
| Bus Drop 8/3 | 3 × 8 AWG + 3G | 3×14 AWG Gd · 50 A | 15.24 | 248 | 415 | 91.4 | Bus Drop Cable size schedule
| Bus Drop 6/3 | 3 × 6 AWG + 3G | 3×12 AWG Gd · 65 A | 17.53 | 395 | 610 | 105.2 | Bus Drop Cable size schedule
| Bus Drop 4/3 | 3 × 4 AWG + 3G | 3×12 AWG Gd · 85 A | 20.83 | 602 | 890 | 125 | Bus Drop Cable size schedule
| Bus Drop 2/3 | 3 × 2 AWG + 3G | 3×10 AWG Gd · 115 A | 23.88 | 955 | 1340 | 143.3 | Bus Drop Cable size schedule
Dimensions and tolerances conform to UL 44 / UL 62 / CSA C22.2 No. 49 / NEC Art. 368.

## Electrical data
Bus Drop Cable – Electrical data (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/bus-drop-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 / UL 62 / CSA C22.2 No. 49 / NEC Art. 368. Values for your order are confirmed in the quotation.
3 Phase + 3 Split Ground | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
3 × 14 AWG + 3G | 8.45 | 20 | 16
3 × 12 AWG + 3G | 5.31 | 25 | 20
3 × 10 AWG + 3G | 3.34 | 35 | 28
3 × 8 AWG + 3G | 2.1 | 50 | 40
3 × 6 AWG + 3G | 1.32 | 65 | 52
3 × 4 AWG + 3G | 0.83 | 85 | 68
3 × 2 AWG + 3G | 0.52 | 115 | 92
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
Bus Drop Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/bus-drop-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 / UL 62 / CSA C22.2 No. 49 / NEC Art. 368. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 600 V AC (3-phase 208 / 480 / 600 V busways)
Key data | Core architecture | 3 Phase + 3 Grou (3 insulated + 3 split bare grounds)
Key data | Phase insulation | PVC + Nylon skin (75 °C wet / 90 °C dry THHN/THWN)
Key data | Gauge range | 14 AWG to 2 AWG (15 A to 115 A machine drops)
Key data | Outer jacket | Oil-resistant PV (-25 / -40 °C to +90 °C FT1/FT4)
Key data | Min. bend radius | 6 × cable OD (Kellems wire-mesh bus-drop grips)
Electrical | Rated voltage | 600 V AC rms
Electrical | Dielectric withstand test | 2.0 kV AC rms for 1 minute
Electrical | Ground path architecture | 3 symmetrical bare copper interstice grounds (combined area per UL 62 Table)
Thermal | Continuous operating temperature | +90 °C dry / +75 °C wet or oil (Oil Resistant I @ 60 °C / Oil II @ 75 °C)
Thermal | Low-temperature rating | -25 °C / -40 °C cold bend
Mechanical | Interstice geometry | True circular triad without bulky 4th-core ovality; high pullout resistance in mesh grips
Mechanical | Minimum bending radius | 6 × overall cable diameter
Resistance | Oil & coolant resistance | UL Oil Resistant I (60 °C) & Oil Resistant II (75 °C) + Nylon hydrocarbon barrier
Resistance | Flame & sunlight resistance | UL 1581 VW-1, CSA FT1 / FT4 flame & UL sunlight resistant
Standards | Governing standards | UL 62, UL 44, CSA C22.2 No. 49 & NEC Article 368.56(B)
Standards | Approvals | UL Listed Bus Drop Cable, CSA Certified, OSHA Acceptable
Identification | Phase conductor colours | Black, White, Red (with 3 bare copper grounds in interstices)
Identification | Outer jacket colour | Black (standard) or Grey/Yellow

## Construction
Bus Drop Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/bus-drop-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 / UL 62 / CSA C22.2 No. 49 / NEC Art. 368. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3 × flexible stranded copper phase cores | Soft annealed bare copper (19-strand or flexible rope-lay) in 14 AWG through 2 AWG per UL 62 / UL 44 | UL 62
2 | Heat & moisture-resistant PVC + Nylon skin | 90 °C dry / 75 °C wet PVC primary dielectric armoured with a clear polyamide Nylon outer skin (Black, White, Red) | UL 44
3 | 3 × bare split copper ground conductors | Three bare stranded copper ground wires positioned symmetrically in the three outer valleys between the phase cores | UL 62
4 | Oil & sunlight-resistant PVC outer jacket | Heavy-duty flame-retardant (VW-1 / FT1), Oil Resistant I & II black PVC outer jacket that grips firmly under wire-mesh bus-drop supports | UL 62
| Standard 600 V Bus Drop Cable (14 AWG to 2 AWG — Black PVC Jacket) | 3 × PVC/Nylon phase conductors (Black, White, Red) + 3 × bare split grounds with black oil-resistant PVC jacket.
| Shielded VFD / EMC Bus Drop Option | Adds an overall aluminum/Mylar tape and tinned copper braid screen over the 3-phase + 3-ground core triad for inverter-fed machines.

## Quality and supply
Bus Drop Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/bus-drop-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 / UL 62 / CSA C22.2 No. 49 / NEC Art. 368. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 2.0 kV AC dielectric test, spark test & DC resistance — Zero breakdown; phase and ground DC resistance verified | 100 % of reels
Sample test | Oil Resistant I/II immersion, Nylon integrity & cold bend — Passes 75 °C oil immersion and mandrel bend | Every batch
Type test | UL VW-1 / CSA FT1/FT4 flame & mesh-grip pullout test — UL Listed Bus Drop Cable to UL 62 / NEC 368.56(B) | Type qualification
Standard / approval | UL Listed Bus Drop Cable (600 V)
Standard / approval | NEC Article 368.56(B) Compliant
Standard / approval | CSA Certified C22.2 No. 49 (FT1 / FT4)
Standard / approval | UL Oil Resistant I & II
Standard / approval | RoHS 3 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) BUS DROP CABLE 3/C [AWG] W/GROUND 600V 90C DRY 75C WET OIL RES I & II VW-1 CSA FT1 [lot/ft]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP