## Request a quote
Request a quotation for CC-Link
Share your protocol/frequency, jacket material (PVC, PUR, LSZH, FEP), and installation motion for CC-Link.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/cc-link-fieldbus-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
CC-Link Fieldbus Cable – Dimensions & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/cc-link-fieldbus-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CLPA CC-Link Specification Ver. 1.10 / Ver. 2.0. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Conductor size | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| CC-Link Ver. 1.10 Fixed PVC 3×20 AWG (0.5 mm²) | 3×20 AWG (Fixed PVC 7.7 mm) | 0.50 mm² (20 AWG) | 7.7 | 36 | 78 | 46 | Standard CC-Link configurations
| CC-Link Ver. 1.10 Movable Flex Oil-PVC 3×20 AWG | 3×20 AWG (Flex Oil-PVC) | 0.50 mm² (20 AWG) | 7.7 | 37 | 80 | 46 | Standard CC-Link configurations
| CC-Link Ver. 1.10 Drag-Chain PUR 3×20 AWG | 3×20 AWG (Drag-Chain PUR) | 0.50 mm² (20 AWG) | 7.8 | 38 | 76 | 47 | Standard CC-Link configurations
| CC-Link Ver. 1.10 Compact Patch 3×22 AWG (0.34 mm²) | 3×22 AWG (Compact Patch) | 0.34 mm² (22 AWG) | 6.5 | 27 | 56 | 39 | Standard CC-Link configurations
| CC-Link Ver. 1.10 + Power Hybrid (3×20 AWG + 2×18 AWG) | 3×20 AWG + 2×18 AWG (Power Hybrid) | 0.50 + 0.75 mm² | 9.6 | 56 | 124 | 58 | Standard CC-Link configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per CLPA CC-Link Specification Ver. 1.10 / Ver. 2.0.

## Impedance, capacitance & attenu
CC-Link Fieldbus Cable – Impedance, capacitance & attenuation (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/cc-link-fieldbus-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CLPA CC-Link Specification Ver. 1.10 / Ver. 2.0. Values for your order are confirmed in the quotation.
Configuration | Impedance Z0 | Max. DC R @ 20 °C Ω/km | Mutual C pF/m ≈ | VoP % | Attenuation @ 20 °C dB/100m | Dielectric test V
3×20 AWG (Fixed PVC 7.7 mm) | 110 Ω | 75.6 | 52 | 75 | 1.6 @ 1 · 4.8 @ 5 · 6.9 @ 10 MHz | 2000
3×20 AWG (Flex Oil-PVC) | 110 Ω | 78 | 52 | 75 | 1.7 @ 1 · 5.0 @ 5 · 7.2 @ 10 MHz | 2000
3×20 AWG (Drag-Chain PUR) | 110 Ω | 78 | 52 | 75 | 1.7 @ 1 · 5.0 @ 5 · 7.2 @ 10 MHz | 2000
3×22 AWG (Compact Patch) | 110 Ω | 110 | 54 | 74 | 2.2 @ 1 · 6.4 @ 5 · 9.2 @ 10 MHz | 1500
3×20 AWG + 2×18 AWG (Power Hybrid) | 110 Ω | 75.6 | 52 | 75 | 1.6 @ 1 · 4.8 @ 5 · 6.9 @ 10 MHz | 2000
Transmission values (characteristic impedance Z0, mutual capacitance, VoP, and attenuation) are measured at +20 °C per CLPA CC-Link Specification Ver. 1.10 / Ver. 2.0.

## Technical data
CC-Link Fieldbus Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/cc-link-fieldbus-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CLPA CC-Link Specification Ver. 1.10 / Ver. 2.0. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Impedance Z0 | 110 Ω ± 15 Ω (At 10 MHz (130 ± 15 Ω @ 1 MHz))
Key data | Core layout | 3 × 20 AWG (DA (Blue) · DB (White) · DG (Yellow))
Key data | Capacitance | < 60 pF / m (≈ 52 pF/m at 1 kHz (foamed PE))
Key data | Attenuation | ≤ 1.6 / 4.8 dB (Per 100 m at 1 MHz / 5 MHz)
Key data | Data rate / reach | 10 Mbps / 1,200 (100 m @ 10 Mbps · 1,200 m @ 156 kbps)
Key data | Shielding | Foil + ≥90% (Al/PET + drain + tinned Cu braid)
Electrical | Characteristic impedance Z0 | 110 Ω ± 15 Ω at 10 MHz (130 Ω ± 15 Ω at 1
Electrical | Max. conductor DC resistance @ 20 °C | ≤ 37.8 Ω/km per core (≤ 75.6 Ω/km loop)
Electrical | Mutual capacitance @ 1 kHz | ≈ 52 pF/m (CLPA limit < 60 pF/m)
Electrical | Velocity of propagation (VoP) | ≈ 75 % (0.75 c) · delay ≤ 4.5 ns/m
Electrical | Attenuation (1 MHz / 5 MHz) | ≤ 1.6 dB/100m @ 1 MHz · ≤ 4.8 dB/100m @ 5 MHz
Electrical | Operating / test voltage | 300 V UL · 2.0 kV AC / 1 min dielectric test
Thermal | Operating temp. (fixed / chain) | -30 °C to +80 °C fixed · -20 °C to +75 °C
Thermal | Storage temperature | -40 °C to +80 °C
Mechanical | Nominal outer diameter | 7.7 mm ± 0.3 mm (standard 3×20 AWG)
Mechanical | Min. bending radius | 6 × D fixed · 10 × D drag-chain
Resistance | Oil & coolant resistance | UL Oil Res 80 °C · EN 60811-404
Resistance | Flame retardancy | UL 1581 VW-1 / CL2 / CM · IEC 60332-1-2
Standards | Primary specification | CLPA CC-Link Cable Specification Ver. 1.10
Standards | Termination resistor value | 110 Ω ± 5 % (1/2 W) for Ver. 1.10 cable
Identification | Core colours (CLPA mandatory) | DA = Blue · DB = White · DG = Yellow + Bare
Identification | Outer sheath colour | Brick Red / Brown (standard) or Matte Black

## Construction
CC-Link Fieldbus Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/cc-link-fieldbus-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CLPA CC-Link Specification Ver. 1.10 / Ver. 2.0. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3 × 20 AWG stranded copper conductors | 7×0.32 mm (0.56 mm², fixed) or 65×0.10 mm / 19×0.18 mm (0.50 mm², drag-chain) | CLPA Ver. 1.10
2 | Foamed polyethylene (FPE) dielectric | Low-permittivity cellular PE in Blue (DA), White (DB), and Yellow (DG) tuned to 110 Ω at | CLPA Ver. 1.10
3 | Al/PET foil + drain wire | 100 % coverage aluminium/polyester tape with stranded tinned copper drain wire (SLD) | CLPA Ver. 1.10
4 | High-density tinned copper braid | Tinned copper wire braid, optical coverage ≥ 90 % | CLPA Ver. 1.10
5 | Outer sheath (7.7 mm OD) | Lead-free flame- and oil-resistant PVC (Brick Red / Brown) or movable Drag-Chain PUR | UL 20276 / CL2 / CM
| CC-Link Ver. 1.10 Standard Fixed PVC (FANC-110SBH eq., 7.7 mm) | 3×20 AWG (7/0.32 mm) 110 Ω fixed trunk cable for trays, conduits, and PLC cabinets.
| CC-Link Ver. 1.10 Movable Drag-Chain PUR / PVC | 3×0.50 mm² extra-fine stranded 110 Ω continuous-flex cable for gantry robots and drag chains.

## Quality and supply
CC-Link Fieldbus Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/cc-link-fieldbus-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CLPA CC-Link Specification Ver. 1.10 / Ver. 2.0. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1 MHz & 10 MHz characteristic impedance & attenuation — Z0 = 110 ± 15 Ω @ 10 MHz (130 ± 15 Ω @ 1 MHz); IL ≤ 1.6 / 4.8 dB/100m @ 1/5 MHz | 100 % of reels
Routine test | DC resistance, capacitance & 2 kV AC dielectric — ≤ 37.8 Ω/km per core; < 60 pF/m; 2.0 kV AC / 1 min | 100 % of reels
Sample test | Braid optical coverage & shield transfer impedance — ≥ 90 % tinned copper braid coverage | Per production batch
Type test | 5-million-cycle drag-chain flex test (PUR variant) — Zero conductor breaks or impedance drift > 10 % | Type approval
Standard / approval | CLPA Ver. 1.10 / Ver. 2.0
Standard / approval | UL AWM 20276 / CL2 / CM
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX CC-LINK VER.1.10 3X20AWG 110 OHM
Supply | Delivery form: Non-returnable plywood reels or export drums
Supply | Standard reel lengths: 100 m · 305 m · 500 m · 1000 m
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP