## Request a quote
Request a quotation for CCS HMWPE Tracer Wire
Underground utility tracer wire engineer
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/copper-clad-steel-hmwpe-direct-burial-locator-tracer-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
CCS HMWPE Tracer Wire – AWG size, temper, break load & jacket wall (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/copper-clad-steel-hmwpe-direct-burial-locator-tracer-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ASTM B869 / ASTM B910 / ASTM D1248 / ICEA S-95-658. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Conductor Size & Temper | Wall mil (mm) | Break Load lbf (N) | DC Res @20°C Ω/km | Overall OD mm (in) | Weight kg/km | Series
| TW-CCS-14AWG-DSA-30 | 14 AWG (1.63 mm) DSA Annealed | 30 (0.76) | 205 (912) | 39.2 | 3.15 (0.124″) | 21.5 | Open-Trench & Light Bore Grades — Annealed (DSA) & High-Strength (HS) 30 mil HMWPE
| TW-CCS-12AWG-DSA-30 | 12 AWG (2.05 mm) DSA Annealed | 30 (0.76) | 300 (1,334) | 24.6 | 3.58 (0.141″) | 31.8 | Open-Trench & Light Bore Grades — Annealed (DSA) & High-Strength (HS) 30 mil HMWPE
| TW-CCS-10AWG-DSA-30 | 10 AWG (2.59 mm) DSA Annealed | 30 (0.76) | 475 (2,113) | 15.5 | 4.11 (0.162″) | 48.2 | Open-Trench & Light Bore Grades — Annealed (DSA) & High-Strength (HS) 30 mil HMWPE
| TW-CCS-14AWG-HS-30 | 14 AWG (1.63 mm) High-Strength | 30 (0.76) | 425 (1,890) | 39.8 | 3.15 (0.124″) | 21.5 | Open-Trench & Light Bore Grades — Annealed (DSA) & High-Strength (HS) 30 mil HMWPE
| TW-CCS-12AWG-HS-30 | 12 AWG (2.05 mm) High-Strength | 30 (0.76) | 680 (3,025) | 25 | 3.58 (0.141″) | 31.8 | Open-Trench & Light Bore Grades — Annealed (DSA) & High-Strength (HS) 30 mil HMWPE
| TW-CCS-12AWG-HS-45 | 12 AWG (2.05 mm) High-Strength | 45 (1.14) | 680 (3,025) | 25 | 4.34 (0.171″) | 36.5 | Open-Trench & Light Bore Grades — Annealed (DSA) & High-Strength (HS) 30 mil HMWPE
| TW-CCS-12AWG-EHS-45 | 12 AWG (2.05 mm) Extra-High-Strength | 45 (1.14) | 1,150 (5,115) | 25.4 | 4.34 (0.171″) | 36.8 | Horizontal Directional Drilling (HDD) & Pipe-Bursting Grades — EHS 45 mil HMWPE/HDPE
| TW-CCS-10AWG-HS-45 | 10 AWG (2.59 mm) High-Strength | 45 (1.14) | 1,100 (4,893) | 15.8 | 4.88 (0.192″) | 53.5 | Horizontal Directional Drilling (HDD) & Pipe-Bursting Grades — EHS 45 mil HMWPE/HDPE
| TW-CCS-10AWG-EHS-45 | 10 AWG (2.59 mm) Extra-High-Strength | 45 (1.14) | 2,030 (9,030) | 16 | 4.88 (0.192″) | 54 | Horizontal Directional Drilling (HDD) & Pipe-Bursting Grades — EHS 45 mil HMWPE/HDPE
| TW-CCS-8AWG-EHS-45 | 8 AWG (3.26 mm) Extra-High-Strength | 45 (1.14) | 2,800 (12,455) | 10.1 | 5.54 (0.218″) | 81.5 | Horizontal Directional Drilling (HDD) & Pipe-Bursting Grades — EHS 45 mil HMWPE/HDPE
| TW-CCS-7X14-EHS-45 | 7×0.064″ Stranded EHS Pipe-Burst | 45 (1.14) | 4,700 (20,906) | 6.2 | 7.16 (0.282″) | 152 | Horizontal Directional Drilling (HDD) & Pipe-Bursting Grades — EHS 45 mil HMWPE/HDPE
| TW-CCS-12AWG-EHS-60 | 12 AWG EHS Rock-Bore 60 mil | 60 (1.52) | 1,150 (5,115) | 25.4 | 5.10 (0.201″) | 42.5 | Horizontal Directional Drilling (HDD) & Pipe-Bursting Grades — EHS 45 mil HMWPE/HDPE
All configurations are stocked in APWA Uniform Color Code jackets: Yellow (Gas), Blue (Potable Water), Green (Sanitary Sewer), Purple (Reclaimed Water), and Orange (Telecom).

## Technical data
CCS HMWPE Tracer Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/copper-clad-steel-hmwpe-direct-burial-locator-tracer-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ASTM B869 / ASTM B910 / ASTM D1248 / ICEA S-95-658. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Conductor | 21% IACS CCS (ASTM B869 copper-clad steel (14–8 AWG))
Key data | Break load | 280–4,700 lbf (1,245 N (14 AWG) to 20.9 kN (8 AWG EHS))
Key data | Jacket wall | 30 or 45 mil (0.76 mm or 1.14 mm virgin HMWPE/HDPE)
Key data | Voltage rating | 30 V / 600 V (Direct-burial underground locator)
Key data | APWA colours | Yellow/Blue/Grn (Gas, Water, Sewer, Reclaimed & Telecom)
Key data | Theft value | Zero Scrap (Deters jobsite copper theft)
Electrical | Conductivity | 21 % IACS minimum at 20 °C (ASTM B869)
Electrical | Rated voltage | 30 V or 600 V direct burial (UL / ICEA S-95-658)
Electrical | In-line DC / AC spark test | 7.5 kV AC / 10 kV DC 100 % spark tested
Electrical | Insulation resistance | ≥ 25,000 MΩ·km at 20 °C
Thermal | Direct-burial temperature rating | −55 °C to +75 °C wet/dry
Thermal | Installation & storage temperature | −40 °C to +70 °C
Mechanical | Gauge range | 14 AWG (1.63 mm), 12 AWG (2.05 mm), 10 AWG (2.59 mm), 8 AWG (3.26 mm)
Mechanical | Break load (12 AWG DSA / HS / EHS) | 300 lbf (1.33 kN) DSA · 680 lbf (3.02 kN) HS · 1,150 lbf (5.12 kN) EHS
Mechanical | Break load (10 AWG / 8 AWG EHS) | 2,030 lbf (9.03 kN) 10 AWG EHS · 2,800–4,700 lbf 8 AWG / 7×EHS
Mechanical | Jacket wall thickness | 30 mil (0.76 mm) or 45 mil (1.14 mm)
Resistance | Environmental stress crack (ESCR) | ASTM D1693 > 1,000 h zero failures
Resistance | Chemical & soil immunity | Resistant to H2S, methane, chlorides, acids & bentonite drilling mud
Standards | Conductor standard | ASTM B869 (Annealed) · ASTM B910 / ASTM B452 (Hard-Drawn)
Standards | Insulation & colour standard | ASTM D1248 · ICEA S-95-658 · APWA Uniform Color Code
Identification | APWA jacket colours | Yellow (Gas), Blue (Water), Green (Sewer), Purple (Reclaimed), Orange (Telecom), Red (Electric)
Identification | Surface legend | TEBAOFLEX [AWG] CCS 21% ASTM B869 [30/45 MIL] HMWPE TRACER WIRE [LBF]
Identification | Customs tariff (HS) | 8544.49 / 7217.30

## Construction
CCS HMWPE Tracer Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/copper-clad-steel-hmwpe-direct-burial-locator-tracer-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ASTM B869 / ASTM B910 / ASTM D1248 / ICEA S-95-658. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | High-strength carbon steel structural core | Low-carbon steel (Dead-Soft Annealed DSA for open trench) or high-carbon steel (Hard-Drawn HS / EHS for directional drilling)
2 | Metallurgical oxygen-free copper cladding (21 % IACS) | Continuous solid copper layer metallurgically diffusion-bonded to the steel core (≥ 3 % of wire radius thickness, 21 % IACS per ASTM B869)
3 | 30 mil or 45 mil HMWPE / HDPE direct-burial jacket | Extruded virgin high-molecular-weight polyethylene (HMWPE) or high-density polyethylene (HDPE) to ASTM D1248 Type I/III Class A/C
| CCS-DSA-30 (Open-Trench Annealed 30 mil HMWPE) | 14, 12 or 10 AWG Dead-Soft Annealed (DSA) 21 % IACS CCS with 30 mil HMWPE jacket for open-cut water, gas and sewer trenches
| CCS-EHS-45 (HDD Extra-High-Strength 45 mil HDPE/HMWPE) | 12, 10 or 8 AWG Hard-Drawn Extra-High-Strength (EHS) 21 % IACS CCS with 45 mil HDPE/HMWPE jacket (1,150–4,700 lbf break load) for HDD

## Quality and supply
CCS HMWPE Tracer Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/copper-clad-steel-hmwpe-direct-burial-locator-tracer-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ASTM B869 / ASTM B910 / ASTM D1248 / ICEA S-95-658. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 7.5 kV AC / 10 kV DC spark & pinhole test — Zero jacket holidays across entire spool length | Every production spool
Routine test | Tensile breaking load & elongation test — Verify rated lbf breaking load (e.g. ≥ 1,150 lbf on 12 AWG EHS) | Every master wire heat
Sample test | Copper cladding thickness & 21 % IACS conductivity test — Metallurgical cross-section ≥ 3 % radius & ≥ 21 % IACS | Production lot
Standard / approval | ASTM B869 / ASTM B910 21% IACS CCS Compliant
Standard / approval | ASTM D1248 / ICEA S-95-658 Direct-Burial Rated
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX [AWG] CCS 21% ASTM B869 [30/45 MIL] HMWPE DIRECT BURIAL TRACER WIRE [LBF]
Supply | Standard spools: 500 ft (152 m), 1,000 ft (305 m) & 2,500 ft (762 m) plastic spools
Supply | APWA colours: Yellow, Blue, Green, Purple, Orange, Red & Black
Supply | Splice accessories: Direct-burial silicone-filled waterproof wire nuts & magnesium ground anodes
Supply | Lead time: 1–2 weeks ex-works