## Request a quote
Request a quotation for CTC Winding Conductor
Power transformer CTC metallurgical engineer
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/continuously-transposed-conductor-ctc-transformer-winding-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
CTC Winding Conductor – Strand count, dimensions, Cu area & wrap (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/continuously-transposed-conductor-ctc-transformer-winding-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60317-0-2 / IEC 60317-12 / IEC 60317-27 / ASTM B272. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Strands × (a × b mm) | Enamel & Bondcoat | Outer Insulation (2t) | Net Cu Area mm² | Overall H × W mm | Bare Cu Wt kg/km | Series
| CTC-11X-1.25X4.5-PVA-P10 | 11 × (1.25 × 4.50) | PVA 120 + Epoxy | 1.0 mm TUP Paper | 60.4 | 9.1 × 10.2 | 537 | HV & Regulating Winding CTC — Paper/TUP Wrapped (11 to 35 Strands)
| CTC-15X-1.40X5.2-PVA-P12 | 15 × (1.40 × 5.20) | PVA 120 + Epoxy | 1.2 mm TUP Paper | 106.8 | 13.0 × 11.8 | 950 | HV & Regulating Winding CTC — Paper/TUP Wrapped (11 to 35 Strands)
| CTC-19X-1.50X6.0-PVA-P15 | 19 × (1.50 × 6.00) | PVA 120 + Epoxy | 1.5 mm TUP Paper | 167.4 | 17.2 × 13.7 | 1488 | HV & Regulating Winding CTC — Paper/TUP Wrapped (11 to 35 Strands)
| CTC-23X-1.60X6.5-PVA-P16 | 23 × (1.60 × 6.50) | PVA 120 + Epoxy | 1.6 mm TUP Paper | 234.6 | 21.6 × 14.8 | 2086 | HV & Regulating Winding CTC — Paper/TUP Wrapped (11 to 35 Strands)
| CTC-29X-1.70X7.2-EI200-P18 | 29 × (1.70 × 7.20) | PEI+PAI 200 + Epoxy | 1.8 mm TUP Paper | 348.9 | 28.2 × 16.4 | 3102 | HV & Regulating Winding CTC — Paper/TUP Wrapped (11 to 35 Strands)
| CTC-35X-1.80X8.0-EI200-P20 | 35 × (1.80 × 8.00) | PEI+PAI 200 + Epoxy | 2.0 mm TUP Paper | 495.5 | 35.6 × 18.2 | 4405 | HV & Regulating Winding CTC — Paper/TUP Wrapped (11 to 35 Strands)
| CTC-39X-1.90X8.5-PVA-NET | 39 × (1.90 × 8.50) | PVA 120 + Epoxy | 0.3 mm Open PET Net | 619.5 | 39.8 × 17.6 | 5507 | High-Current LV, Generator Step-Up (GSU) & HVDC CTC (39 to 75 Strands)
| CTC-45X-2.00X9.0-PVA-P12 | 45 × (2.00 × 9.00) | PVA 120 + Epoxy | 1.2 mm TUP Paper | 796.5 | 48.8 × 19.4 | 7081 | High-Current LV, Generator Step-Up (GSU) & HVDC CTC (39 to 75 Strands)
| CTC-53X-2.00X9.5-EI200-NET | 53 × (2.00 × 9.50) | PEI+PAI 200 + Epoxy | 0.3 mm Glass/PET Net | 991.5 | 56.2 × 19.6 | 8814 | High-Current LV, Generator Step-Up (GSU) & HVDC CTC (39 to 75 Strands)
| CTC-61X-2.10X10.0-PVA-P15 | 61 × (2.10 × 10.0) | PVA 120 + Epoxy | 1.5 mm TUP Paper | 1262.1 | 68.5 × 21.7 | 11220 | High-Current LV, Generator Step-Up (GSU) & HVDC CTC (39 to 75 Strands)
| CTC-69X-2.20X10.5-EI200-P15 | 69 × (2.20 × 10.5) | PEI+PAI 200 + Epoxy | 1.5 mm TUP Paper | 1573.8 | 80.6 × 22.7 | 13991 | High-Current LV, Generator Step-Up (GSU) & HVDC CTC (39 to 75 Strands)
| CTC-75X-2.24X11.2-EI200-NET | 75 × (2.24 × 11.2) | PEI+PAI 200 + Epoxy | 0.4 mm Glass/PET Net | 1858 | 87.8 × 23.1 | 16518 | High-Current LV, Generator Step-Up (GSU) & HVDC CTC (39 to 75 Strands)
Custom strand counts (5 to 85), silver-bearing copper (CuAg 0.1%), controlled Rp0.2 yield strengths (100–280 MPa), and laser-perforated paper wraps are manufactured to coil specification.

## Technical data
CTC Winding Conductor – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/continuously-transposed-conductor-ctc-transformer-winding-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60317-0-2 / IEC 60317-12 / IEC 60317-27 / ASTM B272. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Strand count | 5 to 85 Strands (Odd number (or dual-bundle up to 170))
Key data | Strand size | 1–3.15 × 3–15mm (Thickness × width per IEC 60317-0-2)
Key data | Total Cu area | 30 to 2,500 mm² (High space-factor transformer coil)
Key data | Enamel class | Class 120 / 200 (Oil-compatible IEC 60317-12 / -29)
Key data | Short-circuit | B-Stage Epoxy (Thermo-setting bondcoat cures in coil)
Key data | Outer wrap | Kraft/TUP/Net (2 to 32 paper layers or open PET net)
Electrical | Strand conductivity (20 °C) | ≥ 58.0–58.5 MS/m (≥ 100 % IACS annealed ETP/OFHC Cu)
Electrical | Strand enamel breakdown | ≥ 1,500 V to 3,000 V AC rms per strand (IEC 60317-0-2)
Electrical | Transposition pitch check | 100 % in-line high-frequency strand-to-strand short-circuit monitor
Electrical | Eddy-current loss reduction | 60 % to 85 % lower stray load loss vs parallel flat conductors
Thermal | Enamel thermal class | Class 120 (PVA, IEC 60317-12) · Class 200 (PEI+PAI, IEC 60317-29)
Thermal | Outer wrap thermal class | 105 °C (Kraft) · 120 °C (Thermally Upgraded TUP) · 180 °C (Meta-Aramid)
Thermal | Epoxy bondcoat curing cycle | +115 °C to +135 °C for 6–12 h during coil drying
Mechanical | Number of strands (single CTC) | 5, 7, 9, 11 … up to 85 odd strands (even counts on special order)
Mechanical | Individual strand thickness (a) | 0.80 mm to 3.15 mm (± 0.010 mm precision rolled)
Mechanical | Individual strand width (b) | 2.80 mm to 15.00 mm
Mechanical | Copper proof stress (Rp0.2) | Soft 90–130 MPa · Semi-hard 150–250 MPa · CuAg up to 280 MPa
Mechanical | Epoxy shear bond strength | ≥ 12 MPa at 25 °C · ≥ 3.5 MPa in +100 °C transformer oil
Resistance | Insulating fluid compatibility | Mineral oil (IEC 60296), natural/synthetic ester oil & SF6
Resistance | Hydrolysis resistance | Zero blister or delamination in sealed oil-tube aging test
Standards | Winding wire standards | IEC 60317-0-2 · IEC 60317-12 · IEC 60317-29 · NEMA MW 1000
Standards | Insulating paper standard | IEC 60554-2 · IEEE C57.12.00
Identification | Traceability | Continuous electronic pitch/short-circuit log & drum test report
Identification | Customs tariff (HS) | 8544.11

## Construction
CTC Winding Conductor – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/continuously-transposed-conductor-ctc-transformer-winding-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60317-0-2 / IEC 60317-12 / IEC 60317-27 / ASTM B272. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Rectangular oxygen-free / silver-bearing copper strands | 5 to 85 rectangular ETP or OFHC copper strips (Rp0.2 proof stress 100–260 MPa, or CuAg 0.1 % work-hardened for extreme short-circuit forces)
2 | PVA (Class 120) or PEI+PAI (Class 200) strand enamel | Polyvinyl acetal (Formvar, IEC 60317-12 Class 120) or Polyesterimide + Polyamide-imide (IEC 60317-29 Class 200) Grade 1 or Grade 2 film
3 | Optional B-stage thermosetting epoxy bondcoat & central strip | 15–30 μm semi-cured epoxy resin over the enamel plus a 0.10–0.20 mm central diamond-dotted paper or epoxy-glass divider between the two stacks
4 | Outer multi-layer Kraft / TUP paper or PET net wrapping | 2 to 32 butt-lapped layers of electrical Kraft paper, Thermally Upgraded Kraft (TUP), meta-aramid paper, or open-mesh polyester/glass net
| CTC-PAPER (Kraft / Thermally Upgraded Paper Wrapped) | 5 to 85 PVA or PEI+PAI strands (with or without B-stage epoxy bondcoat) wrapped with 0.5 mm to 3.5 mm total radial Kraft or TUP paper insulation
| CTC-NET (Open Polyester / Fibreglass Net Wrapped) | Epoxy-bondcoated strands held by a semi-open woven PET or glass-fibre net for direct oil cooling in high-current LV windings and shunt reactors

## Quality and supply
CTC Winding Conductor – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/continuously-transposed-conductor-ctc-transformer-winding-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60317-0-2 / IEC 60317-12 / IEC 60317-27 / ASTM B272. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % continuous in-line strand-to-strand short-circuit monitoring — High-frequency bridge monitors every individual strand against all others throughout transposition and paper lapping | 100 % of CTC length
Routine test | Individual strand enamel breakdown, springback & Rp0.2 proof stress — Verify Grade 1/2 dielectric breakdown, 0.2 % yield strength and dimensional tolerance (± 0.01 mm) | Every copper cast & strand spool
Sample test | Epoxy bondcoat curing shear-strength test in +100 °C oil — Verify cured inter-strand shear bond ≥ 12 MPa (25 °C) and ≥ 3.5 MPa (+100 °C) | Every epoxy batch
Standard / approval | IEC 60317-0-2 / IEC 60317-12 (PVA) / IEC 60317-29 (PEI+PAI)
Standard / approval | IEC 60554-2 Electrical Kraft & Thermally Upgraded Paper
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX CTC [N]X[A]X[B] [PVA/EI-AI] [EPOXY] [PAPER/NET] [DRUM SN]
Supply | Delivery form: Precision layer-wound on heavy steel/wooden transformer drums in moisture-barrier bags
Supply | Quality dossier: Full strand Rp0.2 cert, enamel breakdown log, epoxy DSC cure cert & in-line short test log
Supply | Lead time: 3–5 weeks ex-works