## Request a quote
Request a quotation for CU/EPR/HFEVA 0.6/1 kV
Share governing standard (IEC/VDE/UL WTTC/GB/T), voltage rating (0.6/1 kV, 1.8/3 kV or 2,000 V), conductor (Cu or Al) × cross-section, torsion angle and drum length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/cu-epr-hfeva-0-6-1kv-lszh-torsion-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
CU/EPR/HFEVA 0.6/1 kV (Umax 1.2 kV) Unscreened LSZH Wind Turbine Drip- – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/cu-epr-hfeva-0-6-1kv-lszh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Max. pulling kN ≈ | Min. bend R mm | Series
| CU/EPR/HFEVA 0.6/1 kV 1×95 / 4G25 Cu | 1 × 95 mm² (or 4G25 mm² / 3/0 AWG) | IEC 60228 Class 5 Flexible Cu/SnCu | 21.6 | 1080 | 14.2 | 110 | CU/EPR/HFEVA 0.6/1 kV Construction Schedule (−40…+90 °C)
| CU/EPR/HFEVA 0.6/1 kV 1×185 / 4G50 Cu | 1 × 185 mm² (or 4G50 mm² / 373 kcmil) | IEC 60228 Class 5 Flexible Cu/SnCu | 27.8 | 1960 | 27.5 | 140 | CU/EPR/HFEVA 0.6/1 kV Construction Schedule (−40…+90 °C)
| CU/EPR/HFEVA 0.6/1 kV 1×300 / 4G95 Cu | 1 × 300 mm² (or 1×535/777 kcmil) | IEC 60228 Class 5 Flexible Cu/SnCu | 34.6 | 3120 | 45 | 175 | CU/EPR/HFEVA 0.6/1 kV Construction Schedule (−40…+90 °C)
Custom conductor cross-sections, core counts, pre-lugged tower kits and drum lengths available per EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification.

## Electrical & thermal parameters
CU/EPR/HFEVA 0.6/1 kV (Umax 1.2 kV) Unscreened LSZH Wind Turbine Drip- – Electrical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/cu-epr-hfeva-0-6-1kv-lszh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ Ω/km | Rating / Impedance | Operating temp.
1 × 95 mm² (or 4G25 mm² / 3/0 AWG) | 0.206 | 0.6/1 kV (320 A Cu) | −40…+90 °C
1 × 185 mm² (or 4G50 mm² / 373 kcmil) | 0.106 | 0.6/1 kV (495 A Cu) | −40…+90 °C
1 × 300 mm² (or 1×535/777 kcmil) | 0.0641 | 0.6/1 kV (680 A Cu) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, AC high-voltage spark/dielectric and dimensional verification.

## Technical data
CU/EPR/HFEVA 0.6/1 kV (Umax 1.2 kV) Unscreened LSZH Wind Turbine Drip- – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/cu-epr-hfeva-0-6-1kv-lszh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Tested per EN 50525-2-21 / IEC 60502-1)
Key data | Operating temp. | −40…+90 °C (Cold-climate & nacelle wind service)
Key data | Min. bend radius | 5 × OD (Drip-loop, hub & tower routing)
Key data | Core / conductor | Class 5 Flexible (EN 60228 Class 5 finely stranded plain c)
Key data | Outer protection | 5GM5 HF-EVA Halo (Low-smoke zero-halogen thermoset EVA jac)
Key data | Standard | EN 50525-2-21 / (EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind )
Electrical | Rated voltage / operating system | 0.6/1 kV (EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification)
Electrical | Core / conductor construction | Class 5 Flexible Bare Copper (3-5 Cores, 1.5-95 mm²) — EN 60228 Class 5 finely stranded plain copper conductors
Electrical | Primary dielectric / insulation | 3GI3 EPR Core Insulation (0.6/1 kV) — Ethylene-propylene rubber coded Brown, Black, Grey, Green/Yellow
Thermal | Continuous operating temperature | −40…+90 °C (wind turbine nacelle, hub & tower duty)
Thermal | Low-temperature torsion & cold bend | Verified cold-flex and torsion endurance across −40…+90 °C per EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel cable drum
Mechanical | Outer jacket / sheath protection | 5GM5 HF-EVA Halogen-Free Outer Sheath (±144°/m) — Low-smoke zero-halogen thermoset EVA jacket for yaw drip loops
Mechanical | Minimum bending radius | 5 × OD
Mechanical | Intermediate screen / separator / core layer | 3GI3 EPR Core Insulation (0.6/1 kV) — Ethylene-propylene rubber coded Brown, Black, Grey, Green/Yellow
Resistance | Oil, grease, ozone & UV resistance | Resistant to wind turbine gearbox oil, hydraulic fluid, ozone and UV weathering per EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification
Resistance | Flame retardancy & smoke/halogen emission | Flame-retardant and environmental performance verified per EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification
Standards | Conductor & flame/test standards | IEC 60228 / IEC 60332-1-2 & -3 / UL 2277 WTTC / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | CU/EPR/HFEVA 0.6/1 kV
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (5GM5 HF-EVA Halo)
Identification | Customs tariff (HS) | 8544.49 / 8544.60

## Construction
CU/EPR/HFEVA 0.6/1 kV (Umax 1.2 kV) Unscreened LSZH Wind Turbine Drip- – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/cu-epr-hfeva-0-6-1kv-lszh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 Flexible Bare Copper (3-5 Cores, | EN 60228 Class 5 finely stranded plain copper conductors
2 | 3GI3 EPR Core Insulation (0.6/1 kV) | Ethylene-propylene rubber coded Brown, Black, Grey, Green/Yellow
3 | 5GM5 HF-EVA Halogen-Free Outer Sheath (± | Low-smoke zero-halogen thermoset EVA jacket for yaw drip loops
| CU/EPR/HFEVA 0.6/1 kV — Standard Wind Turbine Execution | Built to EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification with class 5 flexible bare copper (3-5 cores, 1.5-95 mm²) and 5gm5 hf-eva halogen-free outer sheath (±144°/m)
| CU/EPR/HFEVA 0.6/1 kV — Pre-Cut Tower / Drip-Loop Kit | Available on bulk export reels or pre-cut to turbine tower section and nacelle drip-loop lengths
| CU/EPR/HFEVA 0.6/1 kV — Cold Torsion & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, conductor DC resistance & cold-torsion qualification report

## Quality and supply
CU/EPR/HFEVA 0.6/1 kV (Umax 1.2 kV) Unscreened LSZH Wind Turbine Drip- – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/cu-epr-hfeva-0-6-1kv-lszh-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification) — DC resistance at 20 °C and insulation/sheath wall thickness within EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification limits | Every manufactured drum length
Routine test | AC high-voltage dielectric & insulation resistance test (EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification) — Zero dielectric breakdown and verified insulation resistance for 0.6/1 kV rating | Every manufactured drum length
Type test | Low-temperature drip-loop torsion, oil & flame qualification (EN 50525-2-21 / VDE 0207 3GI3/5GM5 Wind Drip-Loop Specification) — Verified cold torsion cycle endurance, oil resistance and flame retardancy across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | EN 50525-2-21 / IEC 60502-1 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX CU/EPR/HFEVA 0.6/1 kV EN 50525-2-21 / IEC 60502-1 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel reels or pre-cut wind turbine tower & drip-loop kits
Supply | Standard lengths: 500 m, 1,000 m or custom cut-to-length nacelle drip-loop and tower section sets
Supply | MOQ: 100 m (standard configurations) · 300 m (custom wind builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP