## Request a quote
Request a quotation for ConnectEV SWA
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/armoured-ev-charge-point-power-and-cat5e-hybrid-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
ConnectEV SWA – SWA dimensions, gland size & BS 7671 ampacity (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/armoured-ev-charge-point-power-and-cat5e-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 5467 / BS 6724 / BS 7671 Amendment 2 (Section 722) / EN 50288-2-1. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Power + Data + SWA wire | CW Gland size | Outer Ø ≈ mm | Weight ≈ kg/km | Clipped A | Series
| ConnectEV SWA 3G4.0 + Cat5e | 3×4.0 mm² + Cat5e + 0.9mm SWA | CW 20 | 16.8 | 540 | 42 | Single-Phase 7.4 kW SWA (3G + Cat.5e)
| ConnectEV SWA 3G6.0 + Cat5e | 3×6.0 mm² + Cat5e + 1.25mm SWA | CW 20 | 18.8 | 740 | 53 | Single-Phase 7.4 kW SWA (3G + Cat.5e)
| ConnectEV SWA 3G10.0 + Cat5e | 3×10.0 mm² + Cat5e + 1.25mm SWA | CW 25 | 21.4 | 985 | 73 | Single-Phase 7.4 kW SWA (3G + Cat.5e)
| ConnectEV SWA 3G16.0 + Cat5e | 3×16.0 mm² + Cat5e + 1.25mm SWA | CW 25 | 23.6 | 1290 | 97 | Single-Phase 7.4 kW SWA (3G + Cat.5e)
| ConnectEV SWA 5G6.0 + Cat5e | 5×6.0 mm² + Cat5e + 1.25mm SWA | CW 25 | 21.6 | 960 | 46 | Three-Phase 11 / 22 kW SWA (5G + Cat.5e)
| ConnectEV SWA 5G10.0 + Cat5e | 5×10.0 mm² + Cat5e + 1.25mm SWA | CW 25/32 | 24.8 | 1340 | 63 | Three-Phase 11 / 22 kW SWA (5G + Cat.5e)
| ConnectEV SWA 5G16.0 + Cat5e | 5×16.0 mm² + Cat5e + 1.6mm SWA | CW 32 | 28.4 | 1920 | 85 | Three-Phase 11 / 22 kW SWA (5G + Cat.5e)
4G (3-phase + neutral, using SWA as CPC) and 2-pair Cat.5e CT-only variants are also available.

## Technical data
ConnectEV SWA – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/armoured-ev-charge-point-power-and-cat5e-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 5467 / BS 6724 / BS 7671 Amendment 2 (Section 722) / EN 50288-2-1. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | BS 5467 / BS 672 (BS 7671 Sec. 722 & Reg 522.8.10)
Key data | Power voltage | 0.6 / 1 kV AC (90 °C XLPE power insulation)
Key data | Power sizes | 3G4.0 to 5G16 mm (7.4 kW (1P) & 11–22 kW (3P))
Key data | Data element | Cat.5e F/UTP 4×2 (Screen + 300/500 V inner jacket)
Key data | Armour | Galv. Steel Wire (Earthed mechanical & burial shield)
Key data | Outer sheath | LSZH (BS 6724) / (UV, water & direct-burial rated)
Electrical | Power voltage rating | 0.6 / 1 kV AC (power cores) · 300/500 V sub-jacket on Cat.5e
Electrical | Cat.5e data performance | 100 MHz Category 5e F/UTP · 100 Ω · Ethernet / CT clamp / RS-485
Electrical | Buried / clipped ampacity | 44 A (3G4.0) · 56 A (3G6.0) · 77 A (3G10) · 102 A (3G16) · 67 A (5G10)
Electrical | Dedicated copper PE core | Includes full-size Green/Yellow copper PE core plus earthed SWA armour
Thermal | Max. power conductor temp. | +90 °C continuous (+250 °C short-circuit)
Thermal | Operating ambient range | -25 °C to +70 °C (fixed / buried) · 0 °C to +50 °C (during laying)
Thermal | Ground thermal resistivity | Ampacities rated at standard 20 °C soil and 2.5 K·m/W
Mechanical | SWA wire diameter | 0.9 mm (3G4–5G4) · 1.25 mm (3G6–5G10) · 1.6 mm (5G16)
Mechanical | Min. bend radius | 8 × overall cable OD
Mechanical | BS 6121 SWA gland size | 20S / 20 (3G4, 3G6) · 20 / 25 (3G10, 5G4, 5G6) · 25 / 32 (5G10, 5G16)
Resistance | Direct burial & crush | Concentric steel wire armour resists trench backfill, vehicle load & spades
Resistance | Fire & LSZH performance | BS EN 60332-1-2 / 60332-3-24 · BS EN 60754-1 & BS EN 61034-2 (LSZH)
Resistance | Water & UV resistance | Waterproof polymeric outer sheath UV-stabilized for outdoor risers
Standards | UK armoured cable stds | BS 5467 & BS 6724 · BS 7671 Amendment 2 Section 722
Standards | Data sub-cable standard | EN 50288-2-1 / ISO/IEC 11801 Category 5e F/UTP
Standards | RoHS, REACH & CE / UKCA | 2011/65/EU RoHS 2, REACH, CE & UKCA compliant
Identification | Power core colours | 3G: Brown, Blue, GNYE · 5G: Brown, Black, Grey, Blue, GNYE
Identification | Cat.5e pair colours | 4-pair TIA-568 colour code inside white/blue inner sub-sheath
Identification | Customs tariff (HS) | 8544.4993

## Construction
ConnectEV SWA – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/armoured-ev-charge-point-power-and-cat5e-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 5467 / BS 6724 / BS 7671 Amendment 2 (Section 722) / EN 50288-2-1. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3G, 4G or 5G Class 2 stranded copper power conductors | Stranded plain annealed copper per BS EN 60228 Class 2 (3G4.0, 3G6.0, 3G10, 3G16, 5G4.0, 5G6.0, 5G10, 5G16 mm²)
2 | 90 °C GP8 Cross-Linked Polyethylene (XLPE) power insulation | Thermoset XLPE compound Type GP8 per BS 7655-1.3, colour-coded per BS 7671 / HD 308 S2
3 | Screened Cat.5e F/UTP (4×2×24 AWG) sub-cable + inner bedding | 4-pair 24 AWG copper data cable with Al/PET foil screen, tinned drain wire and 300/500 V inner sheath, laid up with power cores under extruded bedding
4 | Concentric Galvanized Round Steel Wire Armour (SWA) | Single layer of hot-dip galvanized round steel wires (0.9 mm, 1.25 mm or 1.6 mm diameter) per BS EN 10257-1
5 | Black UV-stabilized LSZH (BS 6724) or PVC (BS 5467) outer sheath | Abrasion-, moisture- and UV-resistant Low-Smoke Zero-Halogen (LTS1) or PVC outer sheath with metre markings
| ConnectEV SWA Single-Phase (3G4.0 / 3G6.0 / 3G10 / 3G16 mm² + Cat.5e) | Direct-burial SWA armoured single-phase L+N+PE + screened Cat.5e for 7.4 kW (32 A) domestic driveways and long garden trenches
| ConnectEV SWA Three-Phase (5G4.0 / 5G6.0 / 5G10 / 5G16 mm² + Cat.5e) | Direct-burial SWA armoured three-phase L1+L2+L3+N+PE + screened Cat.5e for 11 kW and 22 kW commercial car park bollards

## Quality and supply
ConnectEV SWA – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/armoured-ev-charge-point-power-and-cat5e-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 5467 / BS 6724 / BS 7671 Amendment 2 (Section 722) / EN 50288-2-1. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 3.5 kV AC power dielectric, 2.5 kV power-to-data hi-pot & Cat.5e sweep — Zero breakdown and zero Cat.5e pair attenuation degradation under SWA | Every manufactured drum
Type test | BS EN 10257-1 galvanized steel wire tensile, torsion & zinc mass test — Armour wires meet BS 5467 mechanical crush and earth continuity limits | Type qualification
Sample test | BS EN 60332-3-24 flame, BS EN 61034-2 smoke & BS EN 60754-1 LSZH test — Meets BS 6724 low-smoke zero-halogen fire safety | Per production batch
Standard / approval | BS 5467 & BS 6724 Compliant
Standard / approval | BS 7671 Sec. 722 & Reg 522.8.10
Standard / approval | CE, UKCA & CPR Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX CONNECT-EV SWA 3G6.0mm2 0.6/1kV XLPE + SCREENED CAT5e SWA LSZH BS 6724 CE UKCA
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP