## Request a quote
Request a quotation for ControlNet RG-6 Quad-Shield
Application engineer · RF coaxial, microwave, shipboard LAN & fieldbus cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/controlnet-quad-shielded-75-ohm-industrial-coaxial-trunk-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
ControlNet RG-6 Quad-Shielded 75 Ω Industrial Coaxial Trunk Cable – Dimensions & weights (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/controlnet-quad-shielded-75-ohm-industrial-coaxial-trunk-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Impedance / size | Conductor & dielectric | Wall ≈ mm | Outer Ø ≈ mm | Metal kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| 3092A Standard Trunk | 75 Ω · 18 AWG Solid | Solid CCS Ø 1.02 + Quad | 0.95 | 7.57 | 32 | 61 | 75 | Standard ControlNet 3092A / 3092F configurations
| 3092F Flex Trunk | 75 Ω · 18 AWG Flex | 19×30 AWG + Quad Shield | 0.95 | 7.62 | 33 | 63 | 76 | Standard ControlNet 3092A / 3092F configurations
| 3092A-CPE Chemical | 75 Ω · 18 AWG CPE | Solid CCS + Quad + CPE | 1 | 7.65 | 32 | 66 | 77 | Standard ControlNet 3092A / 3092F configurations
| 3093A Plenum FEP | 75 Ω · 18 AWG FEP | Solid CCS + Quad + FEP | 0.65 | 6.86 | 32 | 58 | 69 | Standard ControlNet 3092A / 3092F configurations
| 3092A-LSZH | 75 Ω · 18 AWG LSZH | Solid CCS + Quad + LSZH | 0.98 | 7.6 | 32 | 65 | 76 | Standard ControlNet 3092A / 3092F configurations
| 3094A RG-11 Long Trunk | 75 Ω · 14 AWG Solid | Solid CCS Ø 1.63 + Quad | 1.2 | 10.3 | 58 | 112 | 103 | Standard ControlNet 3092A / 3092F configurations
| 3095A Armored Trunk | 75 Ω · 18 AWG AIA | Solid CCS + Quad + Al Armor | 1.35 | 11.8 | 52 | 145 | 118 | Standard ControlNet 3092A / 3092F configurations
| ControlNet Drop Coax | 75 Ω · 20 AWG Flex | Stranded + Quad Tap Cord | 0.85 | 6.9 | 28 | 52 | 55 | Standard ControlNet 3092A / 3092F configurations
Outer diameters and weights are nominal engineering values for ControlNet 3092A / 3092F subject to standard manufacturing tolerances per IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax).

## RF & electrical data
ControlNet RG-6 Quad-Shielded 75 Ω Industrial Coaxial Trunk Cable – RF & electrical data (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/controlnet-quad-shielded-75-ohm-industrial-coaxial-trunk-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Char. Z0 Ω | Velocity VoP / L (% or nH/m) | Dielectric test V AC rms
3092A Standard Trunk (75 Ω · 18 AWG Solid) | 91.9 | 75 | 82 | 2000
3092F Flex Trunk (75 Ω · 18 AWG Flex) | 108 | 75 | 80 | 2000
3092A-CPE Chemical (75 Ω · 18 AWG CPE) | 91.9 | 75 | 82 | 2000
3093A Plenum FEP (75 Ω · 18 AWG FEP) | 91.9 | 75 | 83 | 2000
3092A-LSZH (75 Ω · 18 AWG LSZH) | 91.9 | 75 | 82 | 2000
3094A RG-11 Long Trunk (75 Ω · 14 AWG Solid) | 36.1 | 75 | 82 | 2500
3095A Armored Trunk (75 Ω · 18 AWG AIA) | 91.9 | 75 | 82 | 2000
ControlNet Drop Coax (75 Ω · 20 AWG Flex) | 138 | 75 | 80 | 1500
Characteristic impedance, propagation velocity, DC resistance at +20 °C, and dielectric withstand voltages verified per IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax).

## Technical data
ControlNet RG-6 Quad-Shielded 75 Ω Industrial Coaxial Trunk Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/controlnet-quad-shielded-75-ohm-industrial-coaxial-trunk-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Impedance | 75 Ω ± 2 Ω (RG-6 industrial ControlNet coax)
Key data | Velocity (VoP) | 82 % (53.1 pF/m gas-injected foam PE)
Key data | Shielding | Quad-shield (2 × Al/PET tapes + 60%/40% braids)
Key data | Data rate | 5.0 Mbps (Deterministic CTDMA up to 1000 m)
Key data | Temperature | -30…+75 °C (PVC · up to +200 °C FEP plenum)
Key data | Voltage rating | 300 V RMS (UL CM / CL2 industrial rating)
Electrical | Characteristic impedance | 75 Ω ± 2 Ω
Electrical | Nominal capacitance | 53.1 pF/m (16.2 pF/ft)
Electrical | Velocity of propagation | 82 % nominal (4.06 ns/m delay)
Electrical | Attenuation @ 1 / 5 / 10 MHz | 1.18 / 2.20 / 2.95 dB/100m (3092A)
Electrical | Conductor / shield DC resistance | 91.9 Ω/km center · 17.7 Ω/km quad shield
Thermal | Operating temperature (PVC) | -30 °C to +75 °C (3092A / 3092F)
Thermal | Plenum FEP version (3093A) | -70 °C to +200 °C (UL CMP)
Thermal | UL voltage rating | 300 V RMS (UL CM / CL2)
Mechanical | Conductor / dielectric Ø | 1.02 mm (18 AWG) / 4.57 mm foam PE
Mechanical | Overall diameter | 7.57 mm (0.298 in) nominal
Mechanical | Min. bending radius | 75 mm (10 × OD) installation
Mechanical | Max. pulling tension | 614 N (138 lbf)
Resistance | Flame retardancy | UL 1685 FT4 / UL CMG / IEC 60332-1-2
Resistance | Sunlight & oil resistance | UL Oil Res I & UV sunlight resistant
Resistance | Transfer impedance | Quad-shield Class A++ EMC isolation
Standards | Fieldbus specification | IEC 61158 Type 2 / ODVA ControlNet
Standards | NEC / CEC approvals | NEC CM, CL2 · CEC CMG FT4
Standards | RoHS & REACH | RoHS 3 & REACH SVHC compliant
Identification | Outer jacket colour | Black (standard) or orange (intrinsically safe)
Identification | Jacket legend | TEBAOFLEX 3092A RG-6/U 75 OHM QUAD SHIELD CONTROLNET CM FT4
Identification | Customs tariff (HS) | 8544.20

## Construction
ControlNet RG-6 Quad-Shielded 75 Ω Industrial Coaxial Trunk Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/controlnet-quad-shielded-75-ohm-industrial-coaxial-trunk-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 18 AWG copper-clad steel (CCS) conductor | Solid Ø 1.02 mm CCS (3092A) or 19×30 AWG stranded CCS/alloy (3092F)
2 | Gas-injected foam polyethylene dielectric | Nitrogen-foamed high-density polyethylene (Ø 4.57 mm, 82 % VoP, 53.1 pF/m)
3 | Inner bonded aluminum/polyester/aluminum tape | 100 % coverage bonded aluminum foil tape adhered to dielectric
4 | Dual aluminum braids + second foil shield (Quad) | 60 % Al wire braid + 100 % Al/PET/Al tape + 40 % outer Al wire braid
5 | Industrial PVC, CPE, LSZH or FEP outer jacket | Black sunlight/oil-resistant UL CM/CL2 PVC (Ø 7.57 mm) or harsh-duty CPE/FEP
| 3092A (Solid Trunk) | Solid 18 AWG (1.02 mm) CCS conductor for maximum 1,000 m trunk distance and low attenuation
| 3092F (Flexible Trunk) | Stranded 18 AWG (19×30 AWG) center conductor for flexing panels and high-vibration machinery

## Quality and supply
ControlNet RG-6 Quad-Shielded 75 Ω Industrial Coaxial Trunk Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/controlnet-quad-shielded-75-ohm-industrial-coaxial-trunk-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Characteristic impedance, return loss (VSWR) & TDR sweep — 100 % frequency-domain return loss and TDR impedance verification per IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax) | Every manufactured length
Routine test | Dielectric spark & high-voltage withstand test — 100 % in-line spark and AC/DC dielectric withstand per IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax) | Every spool or drum length
Sample test | Insertion loss (attenuation), velocity & capacitance check — Attenuation (dB/100m), VoP (%), and capacitance within IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax) limits | Per production batch
Type test | Screening attenuation, transfer impedance & environmental qualification — Qualified to IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax) EMC shielding, thermal, and flame/fluid criteria | Type qualification
Standard / approval | IEC 61158 Type 2 / ODVA ControlNet (RG-6 75 Ω Quad-Shield Coax)
Standard / approval | CE (2014/35/EU) & RoHS 3 (2015/863/EU) Compliant
Standard / approval | REACH SVHC Compliance Verified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX 3092A RG-6 75 OHM QUAD SHIELD CONTROLNET TRUNK CABLE CM FT4
Supply | Delivery form: Export wooden drums, flange reels or precision coils
Supply | Standard lengths: 100 m · 305 m · 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP