## Request a quote
Request a quotation for D2X11Y
Application engineer · dynamic reeling cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/d2x11y-0-6-1kv-aramid-reinforced-halogen-free-pur-mining-reeling-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
D2X11Y 0.6/1 kV Aramid-Reinforced PUR Mining Reeling Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/d2x11y-0-6-1kv-aramid-reinforced-halogen-free-pur-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| D2X11Y 3×25 + 3×6G + 2×1.5P | 3×25 + 3×6 (G) + 2×1.5 (P) | Class 5 plain Cu + Aramid | 28.4 | 1380 | 18.5 | 230 | D2X11Y Construction Schedule (-40 to +90 °C)
| D2X11Y 3×35 + 3×6G + 2×1.5P | 3×35 + 3×6 (G) + 2×1.5 (P) | Class 5 plain Cu + Aramid | 31.6 | 1760 | 24 | 255 | D2X11Y Construction Schedule (-40 to +90 °C)
| D2X11Y 3×50 + 3×10G + 2×1.5P | 3×50 + 3×10 (G) + 2×1.5 (P) | Class 5 plain Cu + Aramid | 36.2 | 2440 | 32.5 | 290 | D2X11Y Construction Schedule (-40 to +90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2.

## Electrical, optical & thermal p
D2X11Y 0.6/1 kV Aramid-Reinforced PUR Mining Reeling Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/d2x11y-0-6-1kv-aramid-reinforced-halogen-free-pur-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3×25 + 3×6 (G) + 2×1.5 (P) | 0.78 | 0.6/1 kV (131 A) | -40 to +90 °C
3×35 + 3×6 (G) + 2×1.5 (P) | 0.554 | 0.6/1 kV (162 A) | -40 to +90 °C
3×50 + 3×10 (G) + 2×1.5 (P) | 0.386 | 0.6/1 kV (202 A) | -40 to +90 °C
Every production length undergoes routine conductor DC resistance, high-voltage Spark/AC dielectric or OTDR continuity and dimensional verification.

## Technical data
D2X11Y 0.6/1 kV Aramid-Reinforced PUR Mining Reeling Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/d2x11y-0-6-1kv-aramid-reinforced-halogen-free-pur-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (0.6/1 kV LHD & drill rig reeling)
Key data | Operating temp. | -40 to +90 °C (Continuous mining & industrial duty)
Key data | Min. bend radius | 8 × OD (Fixed installation / dynamic routing)
Key data | Core / conductor | 3×25–95+3G+2P (Class 5 Cu + split earth & 2 pilots)
Key data | Outer protection | 11Y Yellow PUR (Halogen-free rock-cut resistant PUR)
Key data | Standard | VDE 0250 / 11Y (DIN VDE 0250 / IEC 60754-1 / 60332-1-2)
Electrical | Rated voltage / transmission duty | 0.6/1 kV (DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2)
Electrical | Core / conductor construction | Central Aramid Core — Polymer-sheathed high-modulus aramid fibre strain-relief core (20–25 N/mm²)
Electrical | Primary dielectric / buffering | Phase Conductors (3×35 mm²) — IEC 60228 Class 5 flexible plain copper with Black, Brown & Grey XLPE (2X)
Thermal | Continuous operating temperature | -40 to +90 °C (mining & industrial service)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Outer Sheath (11Y Halogen-Free PUR) — Dull yellow rock-cut, oil- and abrasion-resistant halogen-free PUR jacket
Mechanical | Minimum bending radius | 8 × OD
Mechanical | Crush, impact & abrasion duty | Heavy-duty mining rock-cut, impact and tensile protection per DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2
Resistance | Flame retardancy & mine fire safety | Self-extinguishing / flame-retardant mining jacket per DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2
Resistance | Mine water, oil & chemical resistance | Resistant to acidic mine water, hydraulic oils and abrasion per DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2
Standards | Flame & environmental test standards | IEC 60332 / MSHA / EN 60794 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | D2X11Y
Identification | Sheath colour & metre marking | Continuous metre-marked yellow mining outer sheath
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
D2X11Y 0.6/1 kV Aramid-Reinforced PUR Mining Reeling Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/d2x11y-0-6-1kv-aramid-reinforced-halogen-free-pur-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Central Aramid Core | Polymer-sheathed high-modulus aramid fibre strain-relief core (20–25 N/mm²)
2 | Phase Conductors (3×35 mm²) | IEC 60228 Class 5 flexible plain copper with Black, Brown & Grey XLPE (2X)
3 | Split Earth & Pilot Cores | 3 × 6 mm² Green/Yellow XLPE earth cores + 2 × 1.5 mm² White/Blue XLPE pilots
4 | Inner Polyurethane Sheath | Extruded high-elasticity special PUR inner bedding locking core geometry
5 | Outer Sheath (11Y Halogen-Free PUR) | Dull yellow rock-cut, oil- and abrasion-resistant halogen-free PUR jacket
| D2X11Y — Standard Mining Execution | Built to DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2 with central aramid core and outer sheath (11y halogen-free pur)
| D2X11Y — Custom Drum Length & Gland Kit | Available in custom shaft/roadway drum lengths or pre-terminated assemblies
| D2X11Y — Routine & Flame Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & flame test report

## Quality and supply
D2X11Y 0.6/1 kV Aramid-Reinforced PUR Mining Reeling Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/d2x11y-0-6-1kv-aramid-reinforced-halogen-free-pur-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2) — DC resistance at 20 °C / optical attenuation and outer diameter within DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2) — Zero dielectric breakdown and verified insulation resistance over full production length | Every manufactured drum length
Type test | Flame propagation, mechanical crush & thermal ageing qualification (DIN VDE 0250 / IEC 60754-1 / IEC 60332-1-2) — Verified flame retardancy, mechanical integrity and thermal endurance across -40 to +90 °C | Type qualification & periodic lot audit
Standard / approval | VDE 0250 / 11Y Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX D2X11Y VDE 0250 / 11Y 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel mine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shaft/reeling lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP